## Restaurant Inspection Data
Inspection Completed Date | Inspection Number | Inspection Reinspection Number | Inspection Reason | Inspection Open Violations Count | Inspection Passed Flag | Inspection Staff Hours | Inspection Total Violations Count | Inspection Violation Article | Inspection Violation Category | Inspection Violation Code | Inspection Violation Comments | Inspection Violation Description | Inspection Violation Location | Occupant Name | Occupant ID | Occupant Full Street Address | Location Name | Location Auto-Extinguishing System Type | Location Building Auto-Extinguishing System Type List | Location Building Detector Location | Location Building Detector Presence | Location Building Detector Type | Location Building Fire Department Connection (FDC) | Location Building Mix Use Property | Location Building Property Use | Location Building Property Use Category | Location Building Sprinkler Riser | Location Building Standpipe | Location Building Story Above Grade | Location Building Story Below Grade | Location Building Structure Type | Location Full Street Address
| 20180725060 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Waffle House | 3988 | 1162 5TH Southwest Street | 1162 5TH ST SW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1162 5TH Southwest Street
| 20180726066 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Burger King | 13379 | 1181 5TH Southwest Street | 1181 5TH ST SW | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | NO | No | 1 | 0 | Enclosed building | 1181 5TH Southwest Street
| 20180726065 |  | Scheduled | 1 | No |  | 1 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Burger King | 13379 | 1181 5TH Southwest Street | 1181 5TH ST SW | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | NO | No | 1 | 0 | Enclosed building | 1181 5TH Southwest Street
| 20180725061 |  | Scheduled | 1 | No |  | 1 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. |  | Hardee's | 13098 | 1150 5TH Southwest Street | 1150 5TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 1150 5TH Southwest Street
| 20180725062 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Hardee's | 13098 | 1150 5TH Southwest Street | 1150 5TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 1150 5TH Southwest Street
| 20180726076 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Boglas Heights | 1032 | 162 14th Northwest Street | 162 BURNET ST | [14 empty] | 162 BURNET Northwest Street
| 20180726075 |  | Scheduled | 5 | No |  | 5 |  | EMERGENCY - Maintenance | 604.3 |  | Emergency and standby power systems shall be maintained in accordance with NFPA 110 and NFPA 111 such that the system is capable of supplying service within the time specified for the type and duration required. |  | Boglas Heights | 1032 | 162 14th Northwest Street | 162 BURNET ST | [14 empty] | 162 BURNET Northwest Street
| 20180726075 |  | Scheduled | 5 | No |  | 5 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. |  | Boglas Heights | 1032 | 162 14th Northwest Street | 162 BURNET ST | [14 empty] | 162 BURNET Northwest Street
| 20180726075 |  | Scheduled | 5 | No |  | 5 |  | GENERAL - Means of egress | 315.3.2 |  | Combustible materials shall not be stored in exits or enclosures for stairways and ramps. |  | Boglas Heights | 1032 | 162 14th Northwest Street | 162 BURNET ST | [14 empty] | 162 BURNET Northwest Street
| 20180726075 |  | Scheduled | 5 | No |  | 5 |  | PORTABLE - Conspicuous location | 906.5 |  | Portable fire extinguishers shall be located in conspicuous locations where they will be readily accessible and immediately available for use. These locations shall be along normal paths of travel, unless the fire code official determines that the hazard posed indicates the need for placement away from normal paths of travel. |  | Boglas Heights | 1032 | 162 14th Northwest Street | 162 BURNET ST | [14 empty] | 162 BURNET Northwest Street
| 20180726075 |  | Scheduled | 5 | No |  | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | Boglas Heights | 1032 | 162 14th Northwest Street | 162 BURNET ST | [14 empty] | 162 BURNET Northwest Street
| 20180726069 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
| 20180726067 |  | Scheduled | 2 | No |  | 2 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
| 20180726067 |  | Scheduled | 2 | No |  | 2 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. |  | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
| 20180727077 |  | Scheduled | 2 | No |  | 2 |  | ALTERNATIVE - System test | 904.5.1 |  | Systems shall be inspected and tested for proper operation at six-month intervals. Tests shall include a check of the detection system, alarms and releasing devices, including manual stations and other associated equipment. Extinguishing system units shall be weighed and the required amount of agent verified. Stored pressure-type units shall be checked for the required pressure. The cartridge of cartridge-operated units shall be weighed and replaced at intervals indicated by the manufacturer. |  | Poke |  | 101 14th Northwest Street | 101 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other | [5 empty] | Enclosed building | 101 14TH Northwest Street
| 20180727077 |  | Scheduled | 2 | No |  | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Poke |  | 101 14th Northwest Street | 101 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other | [5 empty] | Enclosed building | 101 14TH Northwest Street
| 20180727078 |  | Scheduled | 2 | No |  | 2 |  | ALTERNATIVE - System test | 904.5.1 |  | Systems shall be inspected and tested for proper operation at six-month intervals. Tests shall include a check of the detection system, alarms and releasing devices, including manual stations and other associated equipment. Extinguishing system units shall be weighed and the required amount of agent verified. Stored pressure-type units shall be checked for the required pressure. The cartridge of cartridge-operated units shall be weighed and replaced at intervals indicated by the manufacturer. |  | Poke |  | 101 14th Northwest Street | 101 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other | [5 empty] | Enclosed building | 101 14TH Northwest Street
| 20180727078 |  | Scheduled | 2 | No |  | 2 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Poke |  | 101 14th Northwest Street | 101 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other | [5 empty] | Enclosed building | 101 14TH Northwest Street
|  |  | Scheduled | 1 | No | 0.5 | 1 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Cavalier Diner | 10249 | 1403 EMMET North Street | 1403 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1403 EMMET North Street
| 20180724053 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Champion Taproom |  | 324 6th Southeast Street | 324 6TH ST SE | [14 empty] | 324 6TH Southeast Street
2017-03-15 | 20170315 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-03-15 | 20170315 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | EMERGENCY - Means of egress illumination | 604.2.4 |  | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | Ice Cream Machine | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | EMERGENCY - Means of egress illumination | 604.2.4 |  | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | Ice Cream Machine | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | Kitchen | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | Kitchen | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical panel | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical panel | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Sprinkler room | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 4 | No | 2 | 4 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Sprinkler room | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Throughout | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Pond area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Pond area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Dry chem-Dining area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | ALTERNATIVE - Class K portable fire extinguishers for deep fat fryers | 904.11.5.2 |  | When hazard areas include deep fat fryers, listed Class K portable fire extinguishers shall be provided as follows: 1.For up to four fryers having a maximum cooking medium capacity of 80 pounds (36.3 kg) each: one Class K portable fire extinguisher of a minimum 1.5-gallon ( 6 L) capacity. 2.For every additional group of four fryers having a maximum cooking medium capacity of 80 pounds (36.3 kg) each: one additional Class K portable fire extinguisher of a minimum 1.5-gallon (6 L) capacity shall be provided. 3.For individual fryers exceeding 6 square feet (0.55 m2) in surface area: Class K portable fire extinguishers shall be installed in accordance with the extinguisher manufacturer’s recommendations. | Kitchen | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE | Kitchen | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | MAINTENANCE - Reliability | 1030.2 |  | Required exit accesses, exits and exit discharges shall be continuously maintained free from obstructions or impediments to full instant use in the case of fire or other emergency when the building area served by the means of egress is occupied. An exit or exit passageway shall not be used for any purpose that interferes with a means of egress. | Dining area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | MAINTENANCE - Exit signs | 1030.4 |  | Exit signs shall be installed and maintained in accordance with Section 1011. Decorations, furnishings, equipment or adjacent signage that impairs the visibility of exit signs, creates confusion or prevents identification of the exit shall not be allowed. | Dining area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-04 | 20170404 |  | Scheduled | 9 | No | 2 | 9 |  | OCCUPANT - Posting of occupant load | 1004.3 |  | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. | Seating area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-04-05 | 20170405 |  | Scheduled | 2 | No | 2 | 2 |  | GENERAL - Inspection | 901.6 | Hood system needs inspection | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Kitchen | 2162 BARRACKS RD |  | 2162 BARRACKS Road | 2162 BARRACKS RD | [6 empty] | Not mixed use | Restaurant or cafeteria | [5 empty] | Enclosed building | 2162 BARRACKS Road
2017-04-05 | 20170405 |  | Scheduled | 2 | No | 2 | 2 |  | PORTABLE - General requirements | 906.2 | Extinguisher inspection past due. | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Throughout | 2162 BARRACKS RD |  | 2162 BARRACKS Road | 2162 BARRACKS RD | [6 empty] | Not mixed use | Restaurant or cafeteria | [5 empty] | Enclosed building | 2162 BARRACKS Road
2017-04-07 | 20170407 |  | Scheduled | 3 | No | 2 | 3 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Dining area | Moe's Original BBQ | 10829 | 2119 Ivy Road | 2119 IVY RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 2119 Ivy Road
2017-04-07 | 20170407 |  | Scheduled | 3 | No | 2 | 3 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. |  | Moe's Original BBQ | 10829 | 2119 Ivy Road | 2119 IVY RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 2119 Ivy Road
2017-04-07 | 20170407 |  | Scheduled | 3 | No | 2 | 3 |  | GENERAL - Equipment rooms | 315.3.3 |  | Combustible material shall not be stored in boiler rooms, mechanical rooms or electrical equipment rooms. | Utility room at water heater | Moe's Original BBQ | 10829 | 2119 Ivy Road | 2119 IVY RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 2119 Ivy Road
2017-04-11 | 20170411 |  | Scheduled | 2 | No | 2 | 2 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Kitchen | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2017-04-11 | 20170411 |  | Scheduled | 2 | No | 2 | 2 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Kitchen | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2017-04-11 | 20170411 |  | Scheduled | 2 | No | 2 | 2 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | Sprinkler | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2017-04-11 | 20170411 |  | Scheduled | 2 | No | 2 | 2 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | Sprinkler | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2017-05-15 | 20170515 |  | Scheduled | 5 | No | 2 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | TV | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-05-15 | 20170515 |  | Scheduled | 5 | No | 2 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Freezers | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-05-15 | 20170515 |  | Scheduled | 5 | No | 2 | 5 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Dining area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-05-15 | 20170515 |  | Scheduled | 5 | No | 2 | 5 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. | Kitchen | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-05-15 | 20170515 |  | Scheduled | 5 | No | 2 | 5 |  | MAINTENANCE - Reliability | 1030.2 |  | Required exit accesses, exits and exit discharges shall be continuously maintained free from obstructions or impediments to full instant use in the case of fire or other emergency when the building area served by the means of egress is occupied. An exit or exit passageway shall not be used for any purpose that interferes with a means of egress. | Dining area | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-05-23 | 20170523 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Moe's Original BBQ | 10829 | 2119 Ivy Road | 2119 IVY RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 2119 Ivy Road
2017-05-25 | 20170525 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | 2162 BARRACKS RD |  | 2162 BARRACKS Road | 2162 BARRACKS RD | [6 empty] | Not mixed use | Restaurant or cafeteria | [5 empty] | Enclosed building | 2162 BARRACKS Road
2017-06-02 | 20170602634 |  | Scheduled | 0 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2017-06-02 | 20170602634 |  | Scheduled | 0 | No | 1 | 2 |  | COMMERCIAL - Inspection | 609.3.3.1 | new hood system was installed. | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be inspected at intervals specified in Table 609.3.3.1 or as approved by the fire code official. Inspections shall be completed by qualified individuals. |  | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2017-06-05 | 20170605 |  | Scheduled | 0 | Yes | 2 | 0 | [6 empty] | Bodo's Bagels |  | 1609 University Avenue | 1609 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1609 University Avenue
2017-06-06 | 20170606 |  | Scheduled | 2 | No | 2 | 2 |  | FIRE - Portable fire extinguishers | 2108.4 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and Section 906. A minimum of two, 2-A:10-B:C portable fire extinguishers shall be provided near the doors inside dry cleaning rooms containing Type II, Type III-A and Type III-B dry cleaning systems. CHAPTER 22COMBUSTIBLE DUST-PRODUCING OPERATIONS CHAPTER 22COMBUSTIBLE DUST | Throughout | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2017-06-06 | 20170606 |  | Scheduled | 2 | No | 2 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE | Hood system | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2017-06-06 | 20170606 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2017-06-09 | 20170609 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2017-06-09 | 20170609 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2017-06-21 | 20170621 |  | Scheduled | 1 | No | 2 | 1 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE | Kitchen | Wayside Chicken |  | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2017-06-21 | 20170621 |  | Scheduled | 2 | No | 2 | 2 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Outdoors | Durty Nelly's Deli | 6616 | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2017-06-21 | 20170621 |  | Scheduled | 2 | No | 2 | 2 | [6 empty] | Durty Nelly's Deli | 6616 | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2017-06-21 | 20170621 |  | Scheduled | 0 | No | 2 | 0 | [6 empty] | Fry's Spring Station |  | 2115 Jefferson Park Avenue | 2115 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 | 0 | Enclosed building | 2115 Jefferson Park Avenue
2017-07-05 | 20170705635 |  | Scheduled | 0 | No | 1 | 2 | [6 empty] | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2017-07-27 | 20170727636 |  | Scheduled | 0 | No | 1 | 2 | [6 empty] | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2017-08-01 | 20170801 |  | Scheduled | 1 | No | 2 | 1 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. |  | Durty Nelly's Deli | 6616 | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2017-08-03 | 20170803 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Wayside Chicken |  | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2017-08-03 | 20170813 |  | Scheduled | 0 | Yes | 2 | 0 | [6 empty] | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2017-08-17 | 20180723048 |  | Scheduled | 0 | No |  | 0 | [6 empty] | Marco & Luca Dumpling | 16651 | 107 Elliewood Avenue 1 | 1609 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1609 University Avenue
2017-09-07 | 20170907 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Durty Nelly's Deli | 6616 | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2017-09-07 | 20170907 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Fry's Spring Station |  | 2115 Jefferson Park Avenue | 2115 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 | 0 | Enclosed building | 2115 Jefferson Park Avenue
2017-10-19 | 20171019643 |  | Scheduled | 2 | No | 1 | 5 |  | EMERGENCY - Exit signs | 604.2.3 | reinspected on 11/28/17, 12/18/17 and 03/02/2018. | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | front | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-10-19 | 20171019643 |  | Scheduled | 2 | No | 1 | 5 |  | EMERGENCY - Means of egress illumination | 604.2.4 | reinspected on 11/28/17, 12/18/17 and 03/02/2018. | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | front | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-10-19 | 20171019643 |  | Scheduled | 2 | No | 1 | 5 |  | COMMERCIAL - Extinguishing system service | 609.3.4 | reinspected on 11/28/17, 12/18/17 and 03/02/2018. | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-10-19 | 20171019643 |  | Scheduled | 2 | No | 1 | 5 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-10-19 | 20171019643 |  | Scheduled | 2 | No | 1 | 5 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 | reinspected on 11/28/17, 12/18/17 and 03/02/2018. | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. | kitchen | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-10-19 | 20171019655 |  | Scheduled | 0 | No | 1 | 6 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | front/kitchen | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-10-19 | 20171019655 |  | Scheduled | 0 | No | 1 | 6 |  | EMERGENCY - Means of egress illumination | 604.2.4 |  | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | front/kitchen | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-10-19 | 20171019655 |  | Scheduled | 0 | No | 1 | 6 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-10-19 | 20171019655 |  | Scheduled | 0 | No | 1 | 6 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-10-19 | 20171019655 |  | Scheduled | 0 | No | 1 | 6 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-10-19 | 20171019655 |  | Scheduled | 0 | No | 1 | 6 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-10-24 | 20171024650 |  | Scheduled | 0 | No | 1 | 5 |  | EMERGENCY - Means of egress illumination | 604.2.4 |  | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | front dining area | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-10-24 | 20171024650 |  | Scheduled | 0 | No | 1 | 5 |  | EMERGENCY - Means of egress illumination | 604.2.4 |  | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | kitchen | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-10-24 | 20171024650 |  | Scheduled | 0 | No | 1 | 5 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-10-24 | 20171024650 |  | Scheduled | 0 | No | 1 | 5 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-10-24 | 20171024650 |  | Scheduled | 0 | No | 1 | 5 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | Bar area | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Bar area | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | GENERAL - Storage in buildings | 315.3 |  | Storage of materials in buildings shall be orderly and stacks shall be stable. Storage of combustible materials shall be separated from heaters or heating devices by distance or shielding so that ignition cannot occur. | Kitchen | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | kitchen | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | FIRE - Maintenance | 703.1 |  | The required fire-resistance rating of fire-resistance-rated construction (including walls, fire stops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems) shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced when damaged, altered, breached or penetrated. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | kitchen | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | GENERAL - Ceiling clearance | 315.3.1 |  | Storage shall be maintained 2 feet (610 mm) or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches (457 mm) below sprinkler head deflectors in sprinklered areas of buildings. | kitchen | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-15 | 20171115494 |  | Scheduled | 10 | No | 1 | 10 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Basement | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | hallway main floor | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Basement stairs | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-16 | 20170016497 |  | Scheduled | 7 | No | 1 | 7 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Basement | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2017-11-20 | 20171120656 |  | Scheduled | 0 | No | 1 | 6 | [6 empty] | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-11-28 | 20171128651 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-11-28 | 20171128644 |  | Scheduled | 2 | No | 1 | 5 | [6 empty] | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-11-30 | 20171130620 |  | Scheduled | 2 | No | 1 | 4 |  | EMERGENCY - Means of egress illumination | 604.2.4 | Reinspected on 01/16/18 and 02/05/18. | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. | throughout | The Melting Pot |  | 501 East WATER Street | 501 E WATER ST | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 501 East WATER Street
2017-11-30 | 20171130620 |  | Scheduled | 2 | No | 1 | 4 |  | DOORS - Door operations | 1008.1.9 |  | Except as specifically permitted by this section egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | side exit | The Melting Pot |  | 501 East WATER Street | 501 E WATER ST | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 501 East WATER Street
2017-11-30 | 20171130620 |  | Scheduled | 2 | No | 1 | 4 |  | GENERAL - Securing compressed gas containers | 5303.5.3 |  | Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: 1.Securing containers, cylinders and tanks to a fixed object with one or more restraints. 2.Securing containers, cylinders and tanks on a cart or other mobile device designed for the movement of compressed gas containers, cylinders or tanks. 3.Nesting of compressed gas containers, cylinders and tanks at container filling or servicing facilities or in seller’s warehouses not accessible to the public. Nesting shall be allowed provided the nested containers, cylinders or tanks, if dislodged, do not obstruct the required means of egress. 4.Securing of compressed gas containers, cylinders and tanks to or within a rack, framework, cabinet or similar assembly designed for such use. Exception: Compressed gas containers, cylinders and tanks in the process of examination, filling, transport or servicing. | kitchen prep area | The Melting Pot |  | 501 East WATER Street | 501 E WATER ST | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 501 East WATER Street
2017-11-30 | 20171130620 |  | Scheduled | 2 | No | 1 | 4 |  | MAINTENANCE - Obstructions | 1030.3 | Reinspected on 01/16/18 and 02/05/18. | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. |  | The Melting Pot |  | 501 East WATER Street | 501 E WATER ST | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 501 East WATER Street
2017-12-06 | 20171206657 |  | Scheduled | 0 | No | 1 | 6 | [6 empty] | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2017-12-18 | 20171218645 |  | Scheduled | 2 | No | 1 | 5 | [6 empty] | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2017-12-18 | 20171218652 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2017-12-18 | 20171218495 |  | Scheduled | 5 | No | 1 | 5 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-12-18 | 20171218495 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-12-18 | 20171218495 |  | Scheduled | 5 | No | 1 | 5 |  | FIRE - Maintenance | 703.1 |  | The required fire-resistance rating of fire-resistance-rated construction (including walls, fire stops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems) shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced when damaged, altered, breached or penetrated. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | kitchen | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-12-18 | 20171218495 |  | Scheduled | 5 | No | 1 | 5 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-12-18 | 20171218495 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | kitchen | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2017-12-21 | 20171221499 |  | Scheduled | 7 | No | 1 | 7 | [6 empty] | Escafe | 15469 | 215 West Water Street | 215 W WATER ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 215 West Water Street
2018-01-08 | 20180108648 |  | Scheduled | 0 | No | 1 | 5 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Armando Mexican Restaurant | 12130 | 105 14TH Northwest Street | 105 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 105 14TH Northwest Street
2018-01-08 | 20180108648 |  | Scheduled | 0 | No | 1 | 5 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. |  | Armando Mexican Restaurant | 12130 | 105 14TH Northwest Street | 105 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 105 14TH Northwest Street
2018-01-08 | 20180108648 |  | Scheduled | 0 | No | 1 | 5 |  | EMERGENCY - Means of egress illumination | 604.2.4 |  | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. |  | Armando Mexican Restaurant | 12130 | 105 14TH Northwest Street | 105 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 105 14TH Northwest Street
2018-01-08 | 20180108648 |  | Scheduled | 0 | No | 1 | 5 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) |  | Armando Mexican Restaurant | 12130 | 105 14TH Northwest Street | 105 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 105 14TH Northwest Street
2018-01-08 | 20180108648 |  | Scheduled | 0 | No | 1 | 5 |  | ALTERNATIVE - Operations and maintenance | 904.11.6 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be maintained in accordance with Sections 904.11.6.1 through 904.11.6.3. |  | Armando Mexican Restaurant | 12130 | 105 14TH Northwest Street | 105 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 105 14TH Northwest Street
2018-01-16 | 20180116621 |  | Scheduled | 2 | No | 1 | 4 | [6 empty] | The Melting Pot |  | 501 East WATER Street | 501 E WATER ST | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 501 East WATER Street
2018-01-17 | 20180117649 |  | Scheduled | 0 | Yes | 0 | 5 | [6 empty] | Armando Mexican Restaurant | 12130 | 105 14TH Northwest Street | 105 14TH ST NW | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 105 14TH Northwest Street
2018-02-05 | 20180205622 |  | Scheduled | 2 | No | 1 | 4 | [6 empty] | The Melting Pot |  | 501 East WATER Street | 501 E WATER ST | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 501 East WATER Street
2018-03-05 | 20180305637 |  | Scheduled | 0 | Yes | 1 | 2 | [6 empty] | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-03-05 | 20180305496 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Tastings | 5745 | 502 East MARKET Street | 502 E MARKET ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 502 East MARKET Street
2018-03-05 | 20180305658 |  | Scheduled | 0 | No | 1 | 6 | [6 empty] | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2018-03-05 | 20180305653 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2018-03-07 | 20180307646 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2018-04-16 | 20180416654 |  | Scheduled | 0 | Yes | 1 | 5 | [6 empty] | Fleurie | 18307 | 108 3RD Northeast Street | 106 3RD ST NE |  |  |  | None present |  |  | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 106 3RD Northeast Street
2018-04-16 | 20180416659 |  | Scheduled | 0 | Yes | 1 | 6 | [6 empty] | Petit Pois | 14360 | 201 East MAIN Street A | 201 E MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 201 East MAIN Street
2018-04-30 | 20180430 |  | Scheduled | 1 | No | 2 | 1 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Hood system | 12 ELLIEWOOD AVE |  | 12 ELLIEWOOD Avenue | 12 ELLIEWOOD AVE | Carbon dioxide system | Carbon dioxide system |  |  |  |  | Not mixed use | Restaurant or cafeteria | [5 empty] | Enclosed building | 12 ELLIEWOOD Avenue
2018-05-01 | 20180501647 |  | Scheduled | 0 | Yes | 1 | 5 | [6 empty] | Sal's Cafe Italia | 20684 | 221 East MAIN Street | 221 E MAIN ST | [6 empty] | Assembly use | Assembly, other |  |  |  | 2 |  | Enclosed building | 221 East MAIN Street
2018-05-22 | 20180522437 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-05-22 | 20180522437 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-05-22 | 20180522437 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-05-22 | 20180522437 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-05-22 | 20180522440 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Oakhart Social |  | 511 West MAIN Street | 511 W MAIN ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 511 West MAIN Street
2018-05-24 | 2018052018 |  | Scheduled | 0 | Yes | 2 | 0 | [6 empty] | Korner Restaurant |  | 415 ROOSEVELT BROWN Boulevard | 415 ROOSEVELT BROWN BLVD |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 415 ROOSEVELT BROWN Boulevard
2018-05-24 | 20180524 |  | Scheduled | 0 | Yes | 2 | 0 | [6 empty] | Burger King |  | 1025 SEMINOLE Trail | 1025 SEMINOLE TRL | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1025 SEMINOLE Trail
2018-05-30 | 20180530626 |  | Scheduled | 1 | No | 1 | 3 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). |  | Milan Indian Cuisine | 324 | 1817 EMMET North Street | 1817 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1817 EMMET North Street
2018-05-30 | 20180530626 |  | Scheduled | 1 | No | 1 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Milan Indian Cuisine | 324 | 1817 EMMET North Street | 1817 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1817 EMMET North Street
2018-05-30 | 20180530626 |  | Scheduled | 1 | No | 1 | 3 |  | COMMERCIAL - Ventilation system | 609.3.1 | Fans do not operate when system is tripped. | The ventilation system in connection with hoods shall be operated at the required rate of air movement, and classified grease filters shall be in place when equipment under a kitchen grease hood is used. |  | Milan Indian Cuisine | 324 | 1817 EMMET North Street | 1817 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1817 EMMET North Street
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | water heater | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | water heater | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | front counter | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | front counter | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530623 |  | Scheduled | 3 | No | 1 | 6 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-05-30 | 20180530441 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2018-05-30 | 20180530 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | 12 ELLIEWOOD AVE |  | 12 ELLIEWOOD Avenue | 12 ELLIEWOOD AVE | Carbon dioxide system | Carbon dioxide system |  |  |  |  | Not mixed use | Restaurant or cafeteria | [5 empty] | Enclosed building | 12 ELLIEWOOD Avenue
2018-05-31 | 20180531433 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Stock Provisions |  | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-05-31 | 20180531433 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Stock Provisions |  | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-05-31 | 20180531546 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Doma | 15012 | 709 West Main Street C | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-05-31 | 20180531593 |  | Scheduled | 1 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Bella's | 9463 | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-05-31 | 20180531593 |  | Scheduled | 1 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Bella's | 9463 | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-05-31 | 20180531431 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Continental Divide |  | 811 West Main Street | 817 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 817 MAIN
2018-05-31 | 20180531431 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Continental Divide |  | 811 West Main Street | 817 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 817 MAIN
2018-06-01 | 20180601317 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | 820 W MAIN ST |  | 820 West MAIN Street | 820 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Throughout | Present | Smoke |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 820 West MAIN Street
2018-06-04 | 20180604443 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | World of Beer |  | 852 West Main Street 110 | 852 W MAIN ST | [6 empty] | Business and residential use | Mercantile, business, other |  |  |  | 9 | 0 | Enclosed building | 852 West Main Street
2018-06-04 | 20180604427 |  | Scheduled | 2 | No | 1 | 2 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. |  | Asian Express |  | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-04 | 20180604427 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Asian Express |  | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-04 | 20180604616 |  | Scheduled | 4 | No | 1 | 5 |  | EMERGENCY - Exit signs | 604.2.3 | Reinspected on 07/13/18, 07/30/18, and 09/25/18. Still not corrected. | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. |  | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-04 | 20180604616 |  | Scheduled | 4 | No | 1 | 5 |  | EMERGENCY - Means of egress illumination | 604.2.4 | Reinspected on 07/13/18, 07/30/18, and 09/25/18. Still not corrected. | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. |  | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-04 | 20180604616 |  | Scheduled | 4 | No | 1 | 5 |  | PORTABLE - General requirements | 906.2 | Reinspected on 07/13/18, 07/30/18, and 09/25/18. Still not corrected. | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-04 | 20180604616 |  | Scheduled | 4 | No | 1 | 5 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-04 | 20180604616 |  | Scheduled | 4 | No | 1 | 5 |  | COMMERCIAL - Extinguishing system service | 609.3.4 | Reinspected on 07/13/18, 07/30/18, and 09/25/18. Still not corrected. | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-06-07 | 20180607602 |  | Scheduled | 0 | No | 1 | 5 |  | DOORS - Door operations | 1008.1.9 |  | Except as specifically permitted by this section egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | rear door | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-06-07 | 20180607602 |  | Scheduled | 0 | No | 1 | 5 |  | MAINTENANCE - Finishes | 1030.6 |  | Means of egress doors shall be maintained in such a manner as to be distinguishable from the adjacent construction and finishes such that the doors are easily recognizable as doors. Furnishings, decorations or other objects shall not be placed so as to obstruct exits, access thereto, egress therefrom, or visibility thereof. Hangings and draperies shall not be placed over exit doors or otherwise be located to conceal or obstruct an exit. Mirrors shall not be placed on exit doors. Mirrors shall not be placed in or adjacent to any exit in such a manner as to confuse the direction of exit. | rear exit | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-06-07 | 20180607602 |  | Scheduled | 0 | No | 1 | 5 |  | MAINTENANCE - Obstructions | 1030.3 |  | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | rear exit | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-06-07 | 20180607602 |  | Scheduled | 0 | No | 1 | 5 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-06-07 | 20180607602 |  | Scheduled | 0 | No | 1 | 5 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-06-14 | 20180614404 |  | Scheduled | 1 | No | 1 | 1 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) |  | Mellow Mushroom |  | 1321 West MAIN Street | 1321 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 8 | 1 | Enclosed building | 1321 West MAIN Street
2018-06-14 | 20180614549 |  | Scheduled | 1 | No | 1 | 1 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. | kitchen | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-14 | 20180614545 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Qdoba | 20517 | 1415 UNIVERSITY Avenue A | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-14 | 20180614409 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Roots - kitchen |  | 1400 WERTLAND Street | 1400 WERTLAND ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1400 WERTLAND Street
2018-06-14 | 20180614409 |  | Scheduled | 2 | No | 1 | 2 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Roots - kitchen |  | 1400 WERTLAND Street | 1400 WERTLAND ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1400 WERTLAND Street
2018-06-14 | 20180614361 |  | Scheduled | 4 | No | 1 | 4 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | kitchen | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-06-14 | 20180614361 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-06-14 | 20180614361 |  | Scheduled | 4 | No | 1 | 4 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-06-14 | 20180614361 |  | Scheduled | 4 | No | 1 | 4 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Bar area | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-06-14 | 20180614629 |  | Scheduled | 1 | No | 1 | 1 |  | PORTABLE - General requirements | 906.2 | reinspected on 07/23/18 and 08/16/18. | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | throughout | Five Guys |  | 1119 EMMET North Street | 1119 EMMET ST N | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 1119 EMMET North Street
2018-06-19 | 20180619413 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Ventilation system | 609.3.1 |  | The ventilation system in connection with hoods shall be operated at the required rate of air movement, and classified grease filters shall be in place when equipment under a kitchen grease hood is used. |  | The Virginian |  | 1521 UNIVERSITY | 1521 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 3 | 1 | Enclosed building | 1521 UNIVERSITY
2018-06-19 | 20180619542 |  | Scheduled | 1 | No | 1 | 1 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | Marco & Luca Dumpling | 16651 | 107 Elliewood Avenue 1 | 1609 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1609 University Avenue
2018-06-19 | 20180619444 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Bodo's Bagels |  | 1609 University Avenue | 1609 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1609 University Avenue
2018-06-19 | 20180619551 |  | Scheduled | 5 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | kitchen | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-19 | 20180619551 |  | Scheduled | 5 | No | 1 | 5 |  | OCCUPANT - Posting of occupant load | 1004.3 |  | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. |  | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-19 | 20180619551 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | basement | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-19 | 20180619551 |  | Scheduled | 5 | No | 1 | 5 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | basement | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-19 | 20180619551 |  | Scheduled | 5 | No | 1 | 5 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-06-19 | 20180619411 |  | Scheduled | 1 | No | 1 | 1 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) |  | The Biltmore |  | 16 ELLIEWOOD | 16 ELLIEWOOD AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 16 ELLIEWOOD
2018-06-19 | 20180619403 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Parallel 38 |  | 817 MAIN | 817 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 817 MAIN
2018-06-19 | 20180619547 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | College Inn | 20798 | 1501 University Avenue | 1501 UNIVERSITY AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 1501 University Avenue
2018-06-19 | 20180619547 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | kitchen | College Inn | 20798 | 1501 University Avenue | 1501 UNIVERSITY AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 1501 University Avenue
2018-06-19 | 20180619445 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Trinity Irish Pub |  | 1505 University Avenue | 1501 UNIVERSITY AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 1501 University Avenue
2018-06-20 | 20180620446 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2018-06-20 | 20180620607 |  | Scheduled | 3 | No | 1 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2018-06-20 | 20180620607 |  | Scheduled | 3 | No | 1 | 3 |  | PORTABLE - Where required | 906.1 |  | Portable fire extinguishers shall be installed in the following locations. 1.In Group A, B, E, F, H, I, M, R-1, R-4 and S occupancies. Exceptions: 1.In Groups A, B, and E occupancies equipped throughout with quick response sprinklers, portable fire extinguishers shall be required only in locations specified in Items 2 through 6. 2.In Group I-3 occupancies, portable fire extinguishers shall be permitted to be located at staff locations and the access to such extinguishers shall be permitted to be locked. 2.Within 30 feet (9144 mm) of commercial cooking equipment. 3.In areas where flammable or combustible liquids are stored, used or dispensed. 4.On each floor of structures under construction, except Group R-3 occupancies, in accordance with Section 3315.1. 5.Where required by the sections indicated in Table 906.1. 6.Special-hazard areas, including but not limited to laboratories, computer rooms and generator rooms, where required by the fire code official. Note: In existing buildings, whether fire extinguishers are needed is determined by the USBC or other code in effect when such buildings were constructed. |  | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2018-06-20 | 20180620607 |  | Scheduled | 3 | No | 1 | 3 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) |  | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2018-06-20 | 20180620451 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Tavola | 10783 | 826 HINTON Avenue A | 826 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 826 HINTON Avenue
2018-06-20 | 20180620450 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Moose's | 4269 | 1710 Monticello Road | 1710 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Mixed use, other | Assembly, other |  | No | No | 1 | 0 | Enclosed building | 1710 Monticello Road
2018-06-20 | 20180620390 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Inspection | 609.3.3.1 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be inspected at intervals specified in Table 609.3.3.1 or as approved by the fire code official. Inspections shall be completed by qualified individuals. |  | The Catering Outfit |  | 221 CARLTON Road 8 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-20 | 20180620390 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | The Catering Outfit |  | 221 CARLTON Road 8 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-20 | 20180620430 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-20 | 20180620415 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-06-20 | 20180620415 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-06-20 | 20180620415 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. |  | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-06-20 | 20180620415 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. |  | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-06-20 | 20180620415 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). |  | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-06-20 | 20180620415 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). |  | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-06-20 | 20180620393 |  | Scheduled | 3 | No | 1 | 3 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | JBD Soul Food |  | 816 HINTON | 816 HINTON AVE |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 816 HINTON
2018-06-20 | 20180620393 |  | Scheduled | 3 | No | 1 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | JBD Soul Food |  | 816 HINTON | 816 HINTON AVE |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 816 HINTON
2018-06-20 | 20180620393 |  | Scheduled | 3 | No | 1 | 3 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. |  | JBD Soul Food |  | 816 HINTON | 816 HINTON AVE |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 816 HINTON
2018-06-20 | 20180620419 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2018-06-20 | 20180620419 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2018-06-20 | 20180620419 |  | Scheduled | 2 | No | 1 | 2 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. |  | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2018-06-20 | 20180620419 |  | Scheduled | 2 | No | 1 | 2 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. |  | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2018-06-20 | 20180620447 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Barbie's Burrito Barn | 21240 | 201 Avon Street | 201 AVON ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 201 Avon Street
2018-06-20 | 20180620421 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Fox's Cafe |  | 403 AVON Street | 403 AVON ST |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 403 AVON Street
2018-06-20 | 20180620421 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fox's Cafe |  | 403 AVON Street | 403 AVON ST |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 403 AVON Street
2018-06-20 | 20180620448 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Lampo | 1546 | 205 MONTICELLO Road | 205 MONTICELLO RD |  |  |  | None present |  | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 205 MONTICELLO Road
2018-06-20 | 20180620449 |  | Scheduled | 3 | No | 1 | 3 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | Mas |  | 904 MONTICELLO Road | 904 MONTICELLO RD | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 904 MONTICELLO Road
2018-06-20 | 20180620449 |  | Scheduled | 3 | No | 1 | 3 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Mas |  | 904 MONTICELLO Road | 904 MONTICELLO RD | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 904 MONTICELLO Road
2018-06-20 | 20180620449 |  | Scheduled | 3 | No | 1 | 3 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) |  | Mas |  | 904 MONTICELLO Road | 904 MONTICELLO RD | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 904 MONTICELLO Road
2018-06-20 | 20180620423 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | La Taza |  | 407 MONTICELLO Road B | 407 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 407 MONTICELLO Road
2018-06-21 | 20180621458 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Great Harvest Bread |  | 1701 ALLIED Lane | 1701 ALLIED LN | [6 empty] | Row of stores | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1701 ALLIED Lane
2018-06-21 | 20180621453 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | 1305 LONG ST | 16089 | 1305 Long Street E5 | 1305 LONG ST | [6 empty] | Row of stores | Assembly, other |  |  |  | 1 |  | Enclosed building | 1305 Long Street
2018-06-21 | 20180621457 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Cville Coffee | 6601 | 1301 Harris Street | 1301 HARRIS ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 1301 Harris Street
2018-06-21 | 20180621599 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Mi Canton Restaurant | 5011 | 1703 ALLIED Lane | 1703 ALLIED LN | [6 empty] | Row of stores | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 1703 ALLIED Lane
2018-06-21 | 20180621599 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Mi Canton Restaurant | 5011 | 1703 ALLIED Lane | 1703 ALLIED LN | [6 empty] | Row of stores | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 1703 ALLIED Lane
2018-06-21 | 20180621417 |  | Scheduled | 1 | No | 1 | 1 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) |  | Double Horseshoe Saloon |  | 1522 HIGH | 1522 E HIGH ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1522 HIGH
2018-06-21 | 20180621452 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Fabio's NY Pizza | 13372 | 1551 East High Street | 1551 E HIGH ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 1551 East High Street
2018-06-21 | 20180621454 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Riverside Lunch | 4746 | 1429 Hazel Street | 1429 HAZEL ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 1429 Hazel Street
2018-06-21 | 20180621455 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Jak & Jill | 10523 | 1404 East HIGH Street | 1404 E HIGH ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1404 East HIGH Street
2018-06-21 | 20180621456 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Tubby's | 12366 | 1412 East High Street | 1412 E HIGH ST | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 1412 East High Street
2018-06-21 | 20180621462 |  | Scheduled | 1 | No | 1 | 1 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-06-21 | 20180621462 |  | Scheduled | 1 | No | 1 | 1 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-06-21 | 20180621425 |  | Scheduled | 2 | No | 1 | 2 |  | ELECTRICAL EQUIPMENT, WIRING AND HAZARDS - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-21 | 20180621425 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-21 | 20180621376 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Inspection | 609.3.3.1 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be inspected at intervals specified in Table 609.3.3.1 or as approved by the fire code official. Inspections shall be completed by qualified individuals. |  | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2018-06-21 | 20180621376 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2018-06-21 | 20180621398 |  | Scheduled | 2 | No | 1 | 2 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | La Guadalupana |  | 221 CARLTON 15 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-21 | 20180621398 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | La Guadalupana |  | 221 CARLTON 15 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-06-21 | 20180621460 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Sandy Motley Catering |  | 1717 Allied Lane C | 1717 ALLIED LN | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 1717 ALLIED Lane
2018-06-22 | 20180622470 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Durty Nelly's | 4282 | 2200 Fontaine Avenue | 2200 FONTAINE AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2200 Fontaine Avenue
2018-06-22 | 20180622468 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Durty Nelly's Deli | 6616 | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2018-06-22 | 20180622611 |  | Scheduled | 0 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Wayside Chicken |  | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2018-06-22 | 20180622611 |  | Scheduled | 0 | No | 1 | 2 |  | PORTABLE - Where required | 906.1 |  | Portable fire extinguishers shall be installed in the following locations. 1.In Group A, B, E, F, H, I, M, R-1, R-4 and S occupancies. Exceptions: 1.In Groups A, B, and E occupancies equipped throughout with quick response sprinklers, portable fire extinguishers shall be required only in locations specified in Items 2 through 6. 2.In Group I-3 occupancies, portable fire extinguishers shall be permitted to be located at staff locations and the access to such extinguishers shall be permitted to be locked. 2.Within 30 feet (9144 mm) of commercial cooking equipment. 3.In areas where flammable or combustible liquids are stored, used or dispensed. 4.On each floor of structures under construction, except Group R-3 occupancies, in accordance with Section 3315.1. 5.Where required by the sections indicated in Table 906.1. 6.Special-hazard areas, including but not limited to laboratories, computer rooms and generator rooms, where required by the fire code official. Note: In existing buildings, whether fire extinguishers are needed is determined by the USBC or other code in effect when such buildings were constructed. |  | Wayside Chicken |  | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2018-06-22 | 20180622359 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Guadalajara |  | 2206 FONTAINE | 2206 FONTAINE AVE | [6 empty] | Not mixed use | Eating, drinking places, other | [5 empty] | Enclosed building | 2206 FONTAINE
2018-06-22 | 20180622465 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Silk | 7628 | 2210 FONTAINE Avenue | 2210 FONTAINE AVE | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 2210 FONTAINE Avenue
2018-06-22 | 20180622472 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Wings Over Cville | 4265 | 2029 Ivy Road | 2029 IVY RD | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2029 Ivy Road
2018-06-22 | 20180622474 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Moe's Original BBQ | 10829 | 2119 Ivy Road | 2119 IVY RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 2119 Ivy Road
2018-06-22 | 20180622476 |  | Scheduled | 0 | Yes |  | 0 | [6 empty] | Tokyo Rose | 11971 | 2171 Ivy Road 13 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2018-06-22 | 20180622477 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Taiwan Garden | 10811 | 2171 Ivy Road 9 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2018-06-29 | 20180629459 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Glorious Foods |  | 1709 ALLIED Lane | 1709 ALLIED LN | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 1709 ALLIED Lane
2018-07-02 | 20180702355 |  | Scheduled | 5 | No | 1 | 5 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Waiting area | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-07-02 | 20180702355 |  | Scheduled | 5 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Men's restroom | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-07-02 | 20180702355 |  | Scheduled | 5 | No | 1 | 5 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Kitchen | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-07-02 | 20180702355 |  | Scheduled | 5 | No | 1 | 5 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | storage room | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-07-02 | 20180702355 |  | Scheduled | 5 | No | 1 | 5 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-07-05 | 20180705603 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-07-06 | 20180706483 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Pizza Hut | 6032 | 1001 West Main Street A | 1001 W MAIN ST | [6 empty] | Row of stores | Assembly, other |  |  |  | 1 |  | Enclosed building | 1001 West Main Street
2018-07-06 | 20180706485 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Sugar Shack | 15450 | 1001 West Main Street C | 1001 W MAIN ST | [6 empty] | Row of stores | Assembly, other |  |  |  | 1 |  | Enclosed building | 1001 West Main Street
2018-07-06 | 20180706480 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Fry's Spring Station |  | 2115 Jefferson Park Avenue | 2115 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 | 0 | Enclosed building | 2115 Jefferson Park Avenue
2018-07-06 | 20180706609 |  | Scheduled | 0 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Anna's Pizza | 2916 | 115 MAURY Avenue | 113 MAURY AVE | [6 empty] | Row of stores | Assembly, other |  |  |  | 1 |  | Enclosed building | 115 MAURY Avenue
2018-07-06 | 20180706609 |  | Scheduled | 0 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Anna's Pizza | 2916 | 115 MAURY Avenue | 113 MAURY AVE | [6 empty] | Row of stores | Assembly, other |  |  |  | 1 |  | Enclosed building | 115 MAURY Avenue
2018-07-06 | 20180706482 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2018-07-09 | 20180709613 |  | Scheduled | 3 | No | 1 | 5 |  | EMERGENCY - Exit signs | 604.2.3 | reinspected on 08/16/18 and 09/06/18. not corrected. | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. |  | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-07-09 | 20180709613 |  | Scheduled | 3 | No | 1 | 5 |  | EMERGENCY - Means of egress illumination | 604.2.4 | reinspected on 08/16/18 and 09/06/18. not corrected. | Emergency power shall be provided for means of egress illumination in accordance with Section 1006.3. |  | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-07-09 | 20180709613 |  | Scheduled | 3 | No | 1 | 5 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). |  | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-07-09 | 20180709613 |  | Scheduled | 3 | No | 1 | 5 |  | GENERAL - Storage in buildings | 315.3 |  | Storage of materials in buildings shall be orderly and stacks shall be stable. Storage of combustible materials shall be separated from heaters or heating devices by distance or shielding so that ignition cannot occur. | hot water heater | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-07-09 | 20180709613 |  | Scheduled | 3 | No | 1 | 5 |  | COMMERCIAL - Extinguishing system service | 609.3.4 | reinspected on 08/16/18 and 09/06/18. not corrected. | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-07-09 | 20180709407 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Ming Dynasty |  | 1417 EMMET North Street | 1417 EMMET ST N | [6 empty] | Mixed use, other | Food and beverage sales, grocery store |  |  |  | 2 | 0 | Enclosed building | 1417 EMMET North Street
2018-07-09 | 20180709486 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Super Amanecer | 2643 | 1417 EMMET North Street E | 1417 EMMET ST N | [6 empty] | Mixed use, other | Food and beverage sales, grocery store |  |  |  | 2 | 0 | Enclosed building | 1417 EMMET North Street
2018-07-09 | 20180709591 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Cavalier Diner | 10249 | 1403 EMMET North Street | 1403 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1403 EMMET North Street
2018-07-09 | 20180709591 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Cavalier Diner | 10249 | 1403 EMMET North Street | 1403 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1403 EMMET North Street
2018-07-12 | 20180712492 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2018-07-12 | 20180712493 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Vu Noodles/Pearl Island Catering | 13065 | 233 4TH Northwest Street A | 233 4TH ST NW | Wet-pipe sprinkler system |  | throughout | Present | Smoke |  | Mixed use, other | Assembly, other |  |  |  | 2 | 0 | Enclosed building | 233 4TH Northwest Street
2018-07-12 | 20180712491 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | 505 PRESTON AVE | 15177 | 505 Preston Avenue | 505 PRESTON AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 505 Preston Avenue
2018-07-12 | 20180712633 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Kardinal Hall | 13850 | 722 PRESTON Avenue 104 | 722 PRESTON AVE | Other sprinkler system |  | throughout | Present | Smoke |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 722 PRESTON Avenue
2018-07-12 | 20180712360 |  | Scheduled | 3 | No | 1 | 3 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 |  | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. |  | 13849 |  | 722 PRESTON Avenue 103 | 722 PRESTON AVE | Other sprinkler system |  | throughout | Present | Smoke |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 722 PRESTON Avenue
2018-07-12 | 20180712360 |  | Scheduled | 3 | No | 1 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | 13849 |  | 722 PRESTON Avenue 103 | 722 PRESTON AVE | Other sprinkler system |  | throughout | Present | Smoke |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 722 PRESTON Avenue
2018-07-12 | 20180712360 |  | Scheduled | 3 | No | 1 | 3 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | 13849 |  | 722 PRESTON Avenue 103 | 722 PRESTON AVE | Other sprinkler system |  | throughout | Present | Smoke |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 |  | Enclosed building | 722 PRESTON Avenue
2018-07-13 | 20180713369 |  | Scheduled | 3 | No | 1 | 3 |  | DOORS - Door operations | 1008.1.9 |  | Except as specifically permitted by this section egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | rear exit | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2018-07-13 | 20180713369 |  | Scheduled | 3 | No | 1 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2018-07-13 | 20180713369 |  | Scheduled | 3 | No | 1 | 3 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2018-07-13 | 20180713490 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | 711 HENRY AVE | 11075 | 711 Henry Avenue A | 711 HENRY AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 711 Henry Avenue
2018-07-13 | 20180713600 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2018-07-13 | 20180713600 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2018-07-13 | 20180713489 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Sticks Kebob Shop |  | 917 Preston Avenue A | 917 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 917 Preston Avenue
2018-07-13 | 20180713487 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Bread Works |  | 923 Preston Avenue | 923 PRESTON AVE | Special hazard system, other |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 923 Preston Avenue
2018-07-13 | 20180713436 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Orzo |  | 416 West Main Street | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-07-13 | 20180713436 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Orzo |  | 416 West Main Street | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-07-13 | 20180713439 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-07-13 | 20180713439 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-07-13 | 20180713379 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Public Fish & Oyster |  | 513 MAIN | 513 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 513 MAIN
2018-07-13 | 20180713594 |  | Scheduled | 1 | No | 1 | 2 | [6 empty] | Bella's | 9463 | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-07-13 | 20180713442 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Mel's Cafe |  | 719 West MAIN Street | 719 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 719 West MAIN Street
2018-07-13 | 20180713432 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Continental Divide |  | 811 West Main Street | 817 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 817 MAIN
2018-07-13 | 20180713617 |  | Scheduled | 4 | No | 1 | 5 | [6 empty] | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-07-13 | 20180713428 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Asian Express |  | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-07-13 | 20180713434 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Stock Provisions |  | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-07-13 | 20180713434 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Stock Provisions |  | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-07-18 | 20180718624 |  | Scheduled | 3 | No | 1 | 6 | [6 empty] | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-07-18 | 20180718624 |  | Scheduled | 3 | No | 1 | 6 | [6 empty] | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-07-18 | 20180718627 |  | Scheduled | 1 | No | 1 | 3 | [6 empty] | Milan Indian Cuisine | 324 | 1817 EMMET North Street | 1817 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1817 EMMET North Street
2018-07-23 | 20180723630 |  | Scheduled | 1 | No | 1 | 1 | [6 empty] | Five Guys |  | 1119 EMMET North Street | 1119 EMMET ST N | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 1119 EMMET North Street
2018-07-30 | 20180730435 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Stock Provisions |  | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-07-30 | 20180730429 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Asian Express |  | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-07-30 | 20180730618 |  | Scheduled | 4 | No | 1 | 5 | [6 empty] | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-07-30 | 20180730595 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Bella's | 9463 | 709 West Main Street | 709 W MAIN ST | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 709 West Main Street
2018-07-31 | 20180731422 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Fox's Cafe |  | 403 AVON Street | 403 AVON ST |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 403 AVON Street
2018-07-31 | 20180731426 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-07-31 | 20180731377 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Inspection | 609.3.3.1 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be inspected at intervals specified in Table 609.3.3.1 or as approved by the fire code official. Inspections shall be completed by qualified individuals. |  | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2018-07-31 | 20180731400 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | La Guadalupana |  | 221 CARLTON 15 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-07-31 | 20180731391 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | The Catering Outfit |  | 221 CARLTON Road 8 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-07-31 | 20180731424 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | La Taza |  | 407 MONTICELLO Road B | 407 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 407 MONTICELLO Road
2018-08-03 | 20180803410 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Roots - kitchen |  | 1400 WERTLAND Street | 1400 WERTLAND ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1400 WERTLAND Street
2018-08-03 | 20180803412 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Biltmore |  | 16 ELLIEWOOD | 16 ELLIEWOOD AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 2 | 1 | Enclosed building | 16 ELLIEWOOD
2018-08-03 | 20180803543 |  | Scheduled | 1 | No | 1 | 1 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. | kitchen | Marco & Luca Dumpling | 16651 | 107 Elliewood Avenue 1 | 1609 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1609 University Avenue
2018-08-03 | 20180803414 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Virginian |  | 1521 UNIVERSITY | 1521 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 3 | 1 | Enclosed building | 1521 UNIVERSITY
2018-08-03 | 20180803418 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Double Horseshoe Saloon |  | 1522 HIGH | 1522 E HIGH ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1522 HIGH
2018-08-03 | 20180803550 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Whitespot | 5024 | 1407 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-08-03 | 20180803365 |  | Scheduled | 1 | No | 1 | 1 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Revolutionary Soup |  | 104 14TH 4 | 104 14TH ST NW |  |  |  | Undetermined |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 4 |  | Enclosed building | 104 14TH
2018-08-03 | 20180803552 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-08-03 | 20180803548 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | College Inn | 20798 | 1501 University Avenue | 1501 UNIVERSITY AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 2 |  | Enclosed building | 1501 University Avenue
2018-08-03 | 20180803416 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-08-03 | 20180803416 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2018-08-03 | 20180803420 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2018-08-03 | 20180803420 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2018-08-03 | 20180803394 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | JBD Soul Food |  | 816 HINTON | 816 HINTON AVE |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 816 HINTON
2018-08-03 | 20180803394 |  | Scheduled | 2 | No | 1 | 2 |  | GENERAL - Installation acceptance testing | 901.5 |  | Fire detection and alarm systems, fire-extinguishing systems, fire hydrant systems, fire standpipe systems, fire pump systems, private fire service mains and all other fire protection systems and appurtenances thereto shall be subject to acceptance tests as contained in the installation standards and as approved by the fire code official. The fire code official shall be notified before any required acceptance testing. |  | JBD Soul Food |  | 816 HINTON | 816 HINTON AVE |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 816 HINTON
2018-08-03 | 20180803463 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-08-03 | 20180803463 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2018-08-06 | 20180806362 |  | Scheduled | 1 | No | 1 | 1 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-08-13 | 20180813356 |  | Scheduled | 6 | No | 1 | 6 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | Waiting area | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-08-13 | 20180813356 |  | Scheduled | 6 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | men's restroom | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-08-13 | 20180813356 |  | Scheduled | 6 | No | 1 | 6 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | Kitchen | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-08-13 | 20180813356 |  | Scheduled | 6 | No | 1 | 6 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | storage room | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-08-13 | 20180813356 |  | Scheduled | 6 | No | 1 | 6 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-08-13 | 20180813356 |  | Scheduled | 6 | No | 1 | 6 |  | MAINTENANCE - Obstructions | 1030.3 |  | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. |  | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-08-15 | 20180815405 |  | Scheduled | 2 | No | 1 | 2 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. | kitchen | Mellow Mushroom |  | 1321 West MAIN Street | 1321 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 8 | 1 | Enclosed building | 1321 West MAIN Street
2018-08-15 | 20180815405 |  | Scheduled | 2 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Mellow Mushroom |  | 1321 West MAIN Street | 1321 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 8 | 1 | Enclosed building | 1321 West MAIN Street
2018-08-16 | 20180816628 |  | Scheduled | 1 | No | 1 | 3 | [6 empty] | Milan Indian Cuisine | 324 | 1817 EMMET North Street | 1817 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1817 EMMET North Street
2018-08-16 | 20180816604 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-08-16 | 20180816625 |  | Scheduled | 3 | No | 1 | 6 | [6 empty] | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-08-16 | 20180816625 |  | Scheduled | 3 | No | 1 | 6 | [6 empty] | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2018-08-16 | 2018 816631 |  | Scheduled | 0 | No | 1 | 1 | [6 empty] | Five Guys |  | 1119 EMMET North Street | 1119 EMMET ST N | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 1119 EMMET North Street
2018-08-16 | 20180816614 |  | Scheduled | 3 | No | 1 | 5 | [6 empty] | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-09-06 | 20180906615 |  | Scheduled | 3 | No | 1 | 5 | [6 empty] | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2018-09-06 | 20180906363 |  | Follow-Up | 1 | No | 1 | 1 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-09-06 | 20180906357 |  | Scheduled | 3 | No | 1 | 3 |  | MAINTENANCE - Obstructions | 1030.3 |  | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | Store room exit | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-09-06 | 20180906357 |  | Scheduled | 3 | No | 1 | 3 |  | EMERGENCY - Exit signs | 604.2.3 |  | Emergency power shall be provided for exit signs in accordance with Section 1011.6.3. | Kitchen | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-09-06 | 20180906357 |  | Scheduled | 3 | No | 1 | 3 |  | MAINTENANCE - Obstructions | 1030.3 |  | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. |  | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-09-06 | 20180906605 |  | Scheduled | 0 | No | 1 | 5 | [6 empty] | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-09-06 | 20180906367 |  | Scheduled | 2 | No | 1 | 2 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. |  | LemonGrass |  | 104 14TH 6 | 104 14TH ST NW |  |  |  | Undetermined |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 4 |  | Enclosed building | 104 14TH
2018-09-06 | 20180906367 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | LemonGrass |  | 104 14TH 6 | 104 14TH ST NW |  |  |  | Undetermined |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 4 |  | Enclosed building | 104 14TH
2018-09-10 | 20180910553 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Little John's | 22177 | 1427 UNIVERSITY Avenue | 1413 UNIVERSITY AVE |  |  |  | None present |  |  | Row of stores | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 1413 UNIVERSITY Avenue
2018-09-10 | 20180910406 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Mellow Mushroom |  | 1321 West MAIN Street | 1321 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 8 | 1 | Enclosed building | 1321 West MAIN Street
2018-09-10 | 20180910408 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Ming Dynasty |  | 1417 EMMET North Street | 1417 EMMET ST N | [6 empty] | Mixed use, other | Food and beverage sales, grocery store |  |  |  | 2 | 0 | Enclosed building | 1417 EMMET North Street
2018-09-10 | 20180910592 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Inspection | 609.3.3.1 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be inspected at intervals specified in Table 609.3.3.1 or as approved by the fire code official. Inspections shall be completed by qualified individuals. |  | Cavalier Diner | 10249 | 1403 EMMET North Street | 1403 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1403 EMMET North Street
2018-09-24 | 20180924601 |  | Scheduled | 2 | No | 1 | 2 | [6 empty] | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2018-09-24 | 20180924370 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Marie Bette |  | 700 Rose Hill Dr | Marie Bette Cafe |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 700 Rose Hill Dr
2018-09-24 | 20180924378 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2018-09-24 | 20180924396 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | JBD Soul Food |  | 816 HINTON | 816 HINTON AVE |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 816 HINTON
2018-09-24 | 20180924392 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Catering Outfit |  | 221 CARLTON Road 8 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-09-24 | 20180924401 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | La Guadalupana |  | 221 CARLTON 15 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2018-09-25 | 20180925619 |  | Scheduled | 4 | No | 1 | 5 | [6 empty] | Box'd Kitchen | 13078 | 909 West Main Street | 909 W MAIN ST |  |  |  | None present |  |  | Mixed use, other | Mercantile, business, other |  |  |  | 2 |  | Enclosed building | 909 West Main Street
2018-09-25 | 20180925606 |  | Scheduled | 0 | Yes | 1 | 5 | [6 empty] | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2018-09-25 | 20180925632 |  | Scheduled | 0 | Yes | 1 | 1 | [6 empty] | Five Guys |  | 1119 EMMET North Street | 1119 EMMET ST N | [6 empty] | Row of stores | Mercantile, business, other |  |  |  | 1 |  | Enclosed building | 1119 EMMET North Street
2018-09-27 | 20180927610 |  | Scheduled | 0 | Yes | 1 | 2 | [6 empty] | Anna's Pizza | 2916 | 115 MAURY Avenue | 113 MAURY AVE | [6 empty] | Row of stores | Assembly, other |  |  |  | 1 |  | Enclosed building | 115 MAURY Avenue
2018-09-27 | 20180927612 |  | Scheduled | 0 | Yes | 1 | 2 | [6 empty] | Wayside Chicken |  | 2203 Jefferson Park Avenue | 2203 JEFFERSON PARK AVE | [6 empty] | Mixed use, other | Assembly, other |  |  |  | 1 |  | Enclosed building | 2203 Jefferson Park Avenue
2018-10-08 | 20181008364 |  | Follow-Up | 0 | Yes | 1 | 0 | [6 empty] | Tara Thai |  | 1107 EMMET North Street | 1107 EMMET ST N |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1107 EMMET North Street
2018-10-08 | 20181008358 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Sedona Taphouse |  | 1035 MILLMONT Street | 1035 MILLMONT ST |  |  |  | None present |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1035 MILLMONT Street
2018-10-10 | 20181010544 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Marco & Luca Dumpling | 16651 | 107 Elliewood Avenue 1 | 1609 UNIVERSITY AVE | [6 empty] | Mixed use, other | Restaurant or cafeteria |  |  |  | 1 |  | Enclosed building | 1609 University Avenue
2018-10-10 | 20181010366 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Revolutionary Soup |  | 104 14TH 4 | 104 14TH ST NW |  |  |  | Undetermined |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 4 |  | Enclosed building | 104 14TH
2018-10-10 | 20181010368 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | LemonGrass |  | 104 14TH 6 | 104 14TH ST NW |  |  |  | Undetermined |  |  | Mixed use, other | Restaurant or cafeteria |  |  |  | 4 |  | Enclosed building | 104 14TH
2018-10-10 | 20181010608 |  | Scheduled | 3 | No | 1 | 3 | [6 empty] | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2018-12-17 | 20181217305 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Villa Diner | 13385 | 1250 EMMET North Street | 1250 EMMET ST N | [6 empty] | Not mixed use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 1250 EMMET North Street
2019-02-01 | 201902011139 |  | Scheduled | 0 | No | 1 | 6 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Front entrance | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-02-01 | 201902011139 |  | Scheduled | 0 | No | 1 | 6 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical panel missing blanks | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-02-01 | 201902011139 |  | Scheduled | 0 | No | 1 | 6 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Storeroom Exit | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-02-01 | 201902011139 |  | Scheduled | 0 | No | 1 | 6 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | TV | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-02-01 | 201902011139 |  | Scheduled | 0 | No | 1 | 6 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | TV wall | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-02-01 | 201902011139 |  | Scheduled | 0 | No | 1 | 6 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | 2017-03-06 | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-02-11 | 20190211270 |  | Scheduled | 2 | No | 1 | 2 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Bar Area | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2019-02-11 | 20190211270 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. | Hood system needs cleaning | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2019-03-11 | 20190311271 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Szechuan | 20099 | 2006 HOLIDAY Drive | 2006 HOLIDAY DR |  |  | Throughout | Present | Smoke |  | Assembly use | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 2006 HOLIDAY Drive
2019-03-11 | 201903111140 |  | Scheduled | 0 | No | 0.5 | 6 | [6 empty] | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | MAINTENANCE - Obstructions | 1030.3 |  | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | Front Entrance | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Ceiling Light | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Front Ceiling | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Ceiling Floral Area | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Switch Missing Cover (Rear Exit) | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Electrical panel access (Dish wash area) | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Sprinkler Head (Freezer repair cage) | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-03-13 | 20190313895 |  | Scheduled | 0 | No | 1 | 8 |  | FIRE - Maintenance | 703.1 |  | The required fire-resistance rating of fire-resistance-rated construction (including walls, fire stops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems) shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced when damaged, altered, breached or penetrated. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Repair all ceiling penetrations (pastry area) | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-04-30 | 201904301141 |  | Scheduled | 0 | Yes | 0.5 | 6 | [6 empty] | Champion Brewing Company |  | 324 6TH Southeast Street | 324 6TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side D Upper Lot | Assembly use | Restaurant or cafeteria |  | Side C Medical office Upper level | No | 1 | 1 | Enclosed building | 324 6TH Southeast Street
2019-06-12 | 20190612896 |  | Scheduled | 0 | Yes | 1 | 8 | [6 empty] | Apimento |  | 1304 East MARKET Street C | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-03 | 20190703970 |  | Scheduled | 1 | No | 1 | 1 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. |  | Burger King | 13379 | 1181 5TH Southwest Street | 1181 5TH ST SW | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | NO | No | 1 | 0 | Enclosed building | 1181 5TH Southwest Street
2019-07-03 | 20190703908 |  | Scheduled | 0 | No | 0.74 | 3 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Behind Freezer | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
2019-07-03 | 20190703908 |  | Scheduled | 0 | No | 0.74 | 3 |  | FIRE - Smoke barriers and smoke partitions | 703.1.2 |  | Required smoke barriers and smoke partitions shall be maintained to prevent the passage of smoke. All openings protected with approved smoke barrier doors or smoke dampers shall be maintained in accordance with NFPA 105. | Kitchen area | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
2019-07-03 | 20190703908 |  | Scheduled | 0 | No | 0.74 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | Hood System | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
2019-07-03 | 20190703907 |  | Scheduled | 0 | No | 0.76 | 3 |  | EXIT - Graphics | 1011.6.1 |  | Every exit sign and directional exit sign shall have plainly legible letters not less than 6 inches (152 mm) high with the principal strokes of the letters not less than 3/4 inch (19.1 mm) wide. The word “EXIT” shall have letters having a width not less than 2 inches (51 mm) wide, except the letter “I,” and the minimum spacing between letters shall not be less than 3/8 inch (9.5 mm). Signs larger than the minimum established in this section shall have letter widths, strokes and spacing in proportion to their height. The word “EXIT” shall be in high contrast with the background and shall be clearly discernible when the means of exit sign illumination is or is not energized. If a chevron directional indicator is provided as part of the exit sign, the construction shall be such that the direction of the chevron directional indicator cannot be readily changed. | Left Rear Exit | La Joya |  | 1145 5TH Southwest Street | 1145 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1145 5TH Southwest Street
2019-07-03 | 20190703907 |  | Scheduled | 0 | No | 0.76 | 3 |  | DOORS - Door operations | 1008.1.9 |  | Except as specifically permitted by this section egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | Rear exit door loced | La Joya |  | 1145 5TH Southwest Street | 1145 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1145 5TH Southwest Street
2019-07-03 | 20190703907 |  | Scheduled | 0 | No | 0.76 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | Hood System | La Joya |  | 1145 5TH Southwest Street | 1145 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1145 5TH Southwest Street
2019-07-08 | 20190708911 |  | Scheduled | 0 | No | 1 | 1 |  | ELECTRICAL - Unapproved conditions | 605.6 | Missing Emergency light @ Ansul System box. | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Kitchen | Hardee's | 13098 | 1150 5TH Southwest Street | 1150 5TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 1150 5TH Southwest Street
2019-07-08 | 20190708910 |  | Scheduled | 0 | No | 1 | 1 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front Door/Counter | Taco Bell | 6115 | 1158 5TH Southwest Street | 1158 5TH ST SW |  |  |  | None present |  | No |  | Restaurant or cafeteria |  | No | Side C | 1 | 0 | Enclosed building | 1158 5TH Southwest Street
2019-07-08 | 20190708909 |  | Scheduled | 0 | No | 1 | 1 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Exit/Emergency (Front Entrance | Waffle House | 3988 | 1162 5TH Southwest Street | 1162 5TH ST SW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1162 5TH Southwest Street
2019-07-08 | 20190708912 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Korner Restaurant |  | 415 ROOSEVELT BROWN Boulevard | 415 ROOSEVELT BROWN BLVD |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 415 ROOSEVELT BROWN Boulevard
2019-07-08 | 20190708997 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Ceiling light/Front counter | Brazos Tacos |  | 925 2ND Southeast Street | 925 2ND ST SE | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A | Mixed use, other | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 925 2ND Southeast Street
2019-07-08 | 20190708997 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Coffee/Drink counter closet | Brazos Tacos |  | 925 2ND Southeast Street | 925 2ND ST SE | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A | Mixed use, other | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 925 2ND Southeast Street
2019-07-08 | 20190708997 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). |  | Brazos Tacos |  | 925 2ND Southeast Street | 925 2ND ST SE | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A | Mixed use, other | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 925 2ND Southeast Street
2019-07-08 | 20190708997 |  | Scheduled | 4 | No | 1 | 4 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Class K no date/tag | Brazos Tacos |  | 925 2ND Southeast Street | 925 2ND ST SE | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A | Mixed use, other | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 925 2ND Southeast Street
2019-07-09 | 20190709915 |  | Scheduled | 1 | No | 1 | 4 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Exit/Emergency Combo | Keevil &Keevil Grocery & Kitchen |  | 703 Hinton Avenue | 703 Hinton Ave |  |  |  | None present |  | No | Residential use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 703 Hinton Avenue
2019-07-09 | 20190709915 |  | Scheduled | 1 | No | 1 | 4 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Class K extinguisher (4/18) | Keevil &Keevil Grocery & Kitchen |  | 703 Hinton Avenue | 703 Hinton Ave |  |  |  | None present |  | No | Residential use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 703 Hinton Avenue
2019-07-09 | 20190709915 |  | Scheduled | 1 | No | 1 | 4 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | Hood needs cleaning | Keevil &Keevil Grocery & Kitchen |  | 703 Hinton Avenue | 703 Hinton Ave |  |  |  | None present |  | No | Residential use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 703 Hinton Avenue
2019-07-09 | 20190709915 |  | Scheduled | 1 | No | 1 | 4 |  | COMMERCIAL - Extinguishing system service | 609.3.4 |  | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE | Hood system needs service (4/18) | Keevil &Keevil Grocery & Kitchen |  | 703 Hinton Avenue | 703 Hinton Ave |  |  |  | None present |  | No | Residential use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 703 Hinton Avenue
2019-07-09 | 20190709916 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Fox's Cafe |  | 403 AVON Street | 403 AVON ST |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 403 AVON Street
2019-07-09 | 20190709917 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Lampo | 1546 | 205 MONTICELLO Road | 205 MONTICELLO RD |  |  |  | None present |  | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 205 MONTICELLO Road
2019-07-09 | 20190709918 |  | Scheduled | 0 | No | 1 | 2 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Rear kitchen (side wall) | Royalty Eats |  | 820 CHERRY Avenue | 820 CHERRY AVE |  |  |  | None present |  | No | Mixed use, other | Mercantile, business, other |  | No | No | 1 | 0 | Enclosed building | 820 CHERRY Avenue
2019-07-09 | 20190709918 |  | Scheduled | 0 | No | 1 | 2 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Class K extinguisher | Royalty Eats |  | 820 CHERRY Avenue | 820 CHERRY AVE |  |  |  | None present |  | No | Mixed use, other | Mercantile, business, other |  | No | No | 1 | 0 | Enclosed building | 820 CHERRY Avenue
2019-07-11 | 20190711921 |  | Scheduled | 0 | No | 1 | 2 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Basement/Front of stairs right wall | McDonalds |  | 475 RIDGE MCINTIRE Road | 475 RIDGE MCINTIRE Road |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 475 RIDGE MCINTIRE Road
2019-07-11 | 20190711921 |  | Scheduled | 0 | No | 1 | 2 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Basement | McDonalds |  | 475 RIDGE MCINTIRE Road | 475 RIDGE MCINTIRE Road |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 475 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Bar/TV/Open sign | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Freezer/Side Prep | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Outlet cover (table 34) | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Attic (fan used to cool motor) | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | ELECTRICAL - Unapproved conditions | 605.6 | Open junction box & Open motor housing | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Storage attic area X 2 | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Switch missing cover | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Server station | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711923 |  | Scheduled | 2 | No | 1 | 9 |  | FIRE - Ceilings | 703.3 |  | The hanging and displaying of salable goods and other decorative materials from acoustical ceiling systems that are part of a fire-resistance-rated floor/ceiling or roof/ceiling assembly, shall be prohibited. | Burlap ceiling covering | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-07-11 | 20190711922 |  | Scheduled | 2 | No | 1 | 3 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | kitchen at office | Wendy's |  | 416 4TH Northwest Street | 416 4TH ST NW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 416 4TH Northwest Street
2019-07-11 | 20190711922 |  | Scheduled | 2 | No | 1 | 3 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | all 4 hoods | Wendy's |  | 416 4TH Northwest Street | 416 4TH ST NW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 416 4TH Northwest Street
2019-07-11 | 20190711922 |  | Scheduled | 2 | No | 1 | 3 |  | COMMERCIAL - Extinguishing system service | 609.3.4 | All systems Red tagged. | Automatic fire-extinguishing systems protecting commercial cooking systems shall be serviced as required in Section 904.11.6. SECTION 610COMMERCIAL KITCHENCOOKING OIL STORAGE |  | Wendy's |  | 416 4TH Northwest Street | 416 4TH ST NW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 416 4TH Northwest Street
2019-07-29 | 20190729938 |  | Scheduled | 0 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Men's Restroom | Kentucky Fried Chicken |  | 1705 EMMET North Street | 1705 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1705 North EMMET Street
2019-07-29 | 20190729938 |  | Scheduled | 0 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Women's Restroom | Kentucky Fried Chicken |  | 1705 EMMET North Street | 1705 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1705 North EMMET Street
2019-07-29 | 20190729938 |  | Scheduled | 0 | No | 1 | 3 |  | ELECTRICAL - Abatement of electrical hazards | 605.1 |  | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the responsible code official. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. | Panel missing blanks ''Panel PA'' | Kentucky Fried Chicken |  | 1705 EMMET North Street | 1705 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1705 North EMMET Street
2019-07-29 | 20190729939 |  | Scheduled | 0 | No | 1 | 2 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 |  | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. |  | Popeye's |  | 1709 EMMET North Street A | 1709 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1709 EMMET North Street
2019-07-29 | 20190729939 |  | Scheduled | 0 | No | 1 | 2 |  | PORTABLE - General requirements | 906.2 | ''6/18'' | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Popeye's |  | 1709 EMMET North Street A | 1709 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1709 EMMET North Street
2019-07-29 | 20190729937 |  | Scheduled | 1 | No | 1 | 3 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Front wall | Brother's Bar & Grill |  | 2104 ANGUS Road | 2104 ANGUS RD | Other sprinkler system |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 2104 ANGUS Road
2019-07-29 | 20190729937 |  | Scheduled | 1 | No | 1 | 3 |  | ELECTRICAL - Abatement of electrical hazards | 605.1 |  | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the responsible code official. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. | Electrical Panel missing blank cover | Brother's Bar & Grill |  | 2104 ANGUS Road | 2104 ANGUS RD | Other sprinkler system |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 2104 ANGUS Road
2019-07-29 | 20190729937 |  | Scheduled | 1 | No | 1 | 3 |  | ALTERNATIVE - General | 904.1 |  | Automatic fire-extinguishing systems, other than automatic sprinkler systems, shall be designed, installed, inspected, tested and maintained in accordance with the provisions of this section and the applicable referenced standards. | Non UL-300 Hood Suppression System | Brother's Bar & Grill |  | 2104 ANGUS Road | 2104 ANGUS RD | Other sprinkler system |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 2104 ANGUS Road
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | DOORS - Door operations | 1008.1.9 | Side exit door locked (dead bolt) | Except as specifically permitted by this section egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | Side Exit | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 | In ceiling at duct work. | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Dining area | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Class K | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | GENERAL - Inspection | 901.6 | Sprinkler Missing Trim ring. | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Kitchen Storage Area | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | FIRE - Maintenance | 703.1 | Repair drywall hole at water heater | The required fire-resistance rating of fire-resistance-rated construction (including walls, fire stops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems) shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced when damaged, altered, breached or penetrated. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Kitchen storage area | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Rear freezer locatoin | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | DOORS - Door operations | 1008.1.9 |  | Except as specifically permitted by this section egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | Rear exit | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-30 | 20190730951 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency inoperable battery back up. | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Rear exit | Firefly |  | 1304 East MARKET Street A | 1304 E MARKET ST | Wet-pipe sprinkler system |  |  | None present |  | Side A | Business and residential use | Manufacturing, Processing |  | Side A | No | 2 | 0 | Enclosed building | 1304 East MARKET Street
2019-07-31 | 20190731961 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Burger King |  | 1025 SEMINOLE Trail | 1025 SEMINOLE TRL | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1025 SEMINOLE Trail
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | GENERAL - Inspection | 901.6 | Sprinkler inspection out dated | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Sprinkler Inspection (6/29/18) | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | GENERAL - Inspection | 901.6 | Sprinkler inspection out dated | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Sprinkler Inspection (6/29/18) | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | ELECTRICAL - Extension cords | 605.5 | extension cord operating lamp. | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Sprinkler closet | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | ELECTRICAL - Extension cords | 605.5 | extension cord operating lamp. | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Sprinkler closet | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Host counter | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Host counter | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Angus Room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Angus Room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Angus Room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Angus Room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Private rear room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Private rear room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Private rear room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Private rear room | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | ELECTRICAL - Abatement of electrical hazards | 605.1 | electrical wire laying on sprinkler pipe with wire nuts. | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the responsible code official. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. | Kitchen store room/Paper storage | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | ELECTRICAL - Abatement of electrical hazards | 605.1 | electrical wire laying on sprinkler pipe with wire nuts. | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the responsible code official. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. | Kitchen store room/Paper storage | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Kitchen rear exit | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Kitchen rear exit | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen rear exit | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen rear exit | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front cook counter | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731962 |  | Scheduled | 0 | No | 1.5 | 11 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front cook counter | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-07-31 | 20190731960 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | Marco & Luca Dumplings |  | 176 ZAN Road | 176 ZAN RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 176 ZAN Road
2019-08-01 | 20190801963 |  | Scheduled | 2 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency light inoperable battery backup | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front Door | Moose's | 4269 | 1710 Monticello Road | 1710 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Mixed use, other | Assembly, other |  | No | No | 1 | 0 | Enclosed building | 1710 Monticello Road
2019-08-01 | 20190801963 |  | Scheduled | 2 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Side dining area | Moose's | 4269 | 1710 Monticello Road | 1710 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Mixed use, other | Assembly, other |  | No | No | 1 | 0 | Enclosed building | 1710 Monticello Road
2019-08-01 | 20190801963 |  | Scheduled | 2 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen | Moose's | 4269 | 1710 Monticello Road | 1710 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Mixed use, other | Assembly, other |  | No | No | 1 | 0 | Enclosed building | 1710 Monticello Road
2019-08-01 | 20190801964 |  | Scheduled | 3 | No | 1 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Server Station | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801964 |  | Scheduled | 3 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency light inoperable battery backup. | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Hallway Exit | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801964 |  | Scheduled | 3 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Hallway @ Restrooom | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801964 |  | Scheduled | 3 | No | 1 | 5 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | Storage Room | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801964 |  | Scheduled | 3 | No | 1 | 5 |  | PORTABLE - Hangers and brackets | 906.7 | Class K extinguisher. | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Kitchen | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency light inoperable | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front Door | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front Cooler | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Dining Area side wall | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front coutner | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | Rear bar | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Rear Bar | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801965 |  | Scheduled | 7 | No | 1 | 7 |  | PORTABLE - Hangers and brackets | 906.7 | Class K extinguisher | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Kitchen | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-08-01 | 20190801967 |  | Scheduled | 0 | Yes | 1 | 0 | [6 empty] | The Catering Outfit |  | 221 CARLTON Road 8 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801966 |  | Scheduled | 0 | No | 1 | 4 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Rear freezer | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801966 |  | Scheduled | 0 | No | 1 | 4 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | TV | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801966 |  | Scheduled | 0 | No | 1 | 4 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Needs inspection (7/18) | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801966 |  | Scheduled | 0 | No | 1 | 4 |  | PORTABLE - Hangers and brackets | 906.7 | Front door & Kitchen | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Both ABC & K Can | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency light | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front door | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency light | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Side Exit (dining) | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front wall (Juice Machine) | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency light battery back up | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front Coutner | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Abatement of electrical hazards | 605.1 | Panel missing blanks. | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the responsible code official. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. | Storage Room | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency inoperable battery back up | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | No date on extinguishers | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-01 | 20190801968 |  | Scheduled | 7 | No | 1 | 8 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 |  | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. | No Date | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-08-07 | 20190807971 |  | Scheduled | 0 | No | 0.75 | 1 | [6 empty] | Burger King | 13379 | 1181 5TH Southwest Street | 1181 5TH ST SW | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | NO | No | 1 | 0 | Enclosed building | 1181 5TH Southwest Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Host Station | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Through out kitchen area | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Dish wash area | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. | Hood System | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Bar area | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | All extinguishers need annual (5/18) | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | MAINTENANCE - Exit signs | 1030.4 |  | Exit signs shall be installed and maintained in accordance with Section 1011. Decorations, furnishings, equipment or adjacent signage that impairs the visibility of exit signs, creates confusion or prevents identification of the exit shall not be allowed. | Side Dining (exit not visible) | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 20190807987 |  | Scheduled | 0 | No | 1 | 8 |  | OCCUPANT - Posting of occupant load | 1004.3 | Getting from NDS. | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. | No occupancy permit | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-07 | 201908071051 |  | Scheduled | 0 | No | 0.5 | 3 | [6 empty] | La Joya |  | 1145 5TH Southwest Street | 1145 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1145 5TH Southwest Street
2019-08-07 | 201908071053 |  | Scheduled | 0 | No | 0.5 | 3 | [6 empty] | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
2019-08-07 | 2019087988 |  | Scheduled | 0 | No | 1 | 6 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo battery back up | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Front | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-08-07 | 2019087988 |  | Scheduled | 0 | No | 1 | 6 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | All needs inspection (12/17) | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-08-07 | 2019087988 |  | Scheduled | 0 | No | 1 | 6 |  | ELECTRICAL - Power supply | 605.4.2 | Daisy chain power strip | Relocatable power taps shall be directly connected to a permanently installed receptacle. | Bar | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-08-07 | 2019087988 |  | Scheduled | 0 | No | 1 | 6 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. |  | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-08-07 | 2019087988 |  | Scheduled | 0 | No | 1 | 6 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 |  | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. | (12/17) | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-08-07 | 2019087988 |  | Scheduled | 0 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Hallway @ restroom | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | FIRE - Existing buildings | 912.2.2 |  | On existing buildings, wherever the fire department connection is not visible to approaching fire apparatus, the fire department connection shall be indicated by an approved sign mounted on the street front or on the side of the building. Such sign shall have the letters “FDC” at least 6 inches (152 mm) high and words in letters at least 2 inches (51 mm) high or an arrow to indicate the location. All such signs shall be subject to the approval of the fire code official. |  | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Bar | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. | Front Hood | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Kitchen (Class K) | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Unable to read date | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | GENERAL - Installation | 901.4 | FDC Needs flushing. Found trash inside piping. | Fire protection systems shall be maintained in accordance with the original installation standards for that system. Required systems shall be extended, altered or augmented as necessary to maintain and continue protection whenever the building is altered, remodeled or added to. Alterations to fire protection systems shall be done in accordance with applicable standards. | FDC need flushing | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | GENERAL - Installation | 901.4 |  | Fire protection systems shall be maintained in accordance with the original installation standards for that system. Required systems shall be extended, altered or augmented as necessary to maintain and continue protection whenever the building is altered, remodeled or added to. Alterations to fire protection systems shall be done in accordance with applicable standards. | FDC Missing caps | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809991 |  | Scheduled | 0 | No | 1 | 8 |  | OCCUPANT - Posting of occupant load | 1004.3 |  | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. |  | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-08-09 | 20190809990 |  | Scheduled | 0 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen wall | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-09 | 20190809990 |  | Scheduled | 0 | No | 1 | 6 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | All | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-09 | 20190809990 |  | Scheduled | 0 | No | 1 | 6 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 |  | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. | 2018-04-26 | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-09 | 20190809990 |  | Scheduled | 0 | No | 1 | 6 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Front entrance | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-09 | 20190809990 |  | Scheduled | 0 | No | 1 | 6 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Kitchen Exit | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-09 | 20190809990 |  | Scheduled | 0 | No | 1 | 6 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. |  | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-08-12 | 20190812989 |  | Scheduled | 4 | No | 1 | 4 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Simply Catering |  | 814 CHERRY Avenue | 814 CHERRY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 814 CHERRY Avenue
2019-08-12 | 20190812989 |  | Scheduled | 4 | No | 1 | 4 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 |  | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. | (8/17) | Simply Catering |  | 814 CHERRY Avenue | 814 CHERRY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 814 CHERRY Avenue
2019-08-12 | 20190812989 |  | Scheduled | 4 | No | 1 | 4 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Class K & ABC (8/17) | Simply Catering |  | 814 CHERRY Avenue | 814 CHERRY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 814 CHERRY Avenue
2019-08-12 | 20190812989 |  | Scheduled | 4 | No | 1 | 4 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | ABC | Simply Catering |  | 814 CHERRY Avenue | 814 CHERRY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 814 CHERRY Avenue
2019-08-14 | 20190814996 |  | Scheduled | 0 | Yes | 0.5 | 1 | [6 empty] | Hardee's | 13098 | 1150 5TH Southwest Street | 1150 5TH ST SW | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 1150 5TH Southwest Street
2019-08-14 | 20190814994 |  | Scheduled | 0 | Yes | 0.5 | 1 | [6 empty] | Waffle House | 3988 | 1162 5TH Southwest Street | 1162 5TH ST SW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1162 5TH Southwest Street
2019-08-14 | 20190814995 |  | Scheduled | 0 | Yes | 0.5 | 1 | [6 empty] | Taco Bell | 6115 | 1158 5TH Southwest Street | 1158 5TH ST SW |  |  |  | None present |  | No |  | Restaurant or cafeteria |  | No | Side C | 1 | 0 | Enclosed building | 1158 5TH Southwest Street
2019-08-14 | 20190814998 |  | Scheduled | 4 | No | 0.5 | 4 | [6 empty] | Brazos Tacos |  | 925 2ND Southeast Street | 925 2ND ST SE | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A | Mixed use, other | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 925 2ND Southeast Street
2019-08-15 | 201908151009 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front (radio) | Maroc & Luca Dumpling |  | 112 West Main Street 15 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151009 |  | Scheduled | 5 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | dining | Maroc & Luca Dumpling |  | 112 West Main Street 15 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151009 |  | Scheduled | 5 | No | 1 | 5 |  | FIRE - Maintenance | 703.1 | Missing ceiling tile. | The required fire-resistance rating of fire-resistance-rated construction (including walls, fire stops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems) shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced when damaged, altered, breached or penetrated. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Hood Vent | Maroc & Luca Dumpling |  | 112 West Main Street 15 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151009 |  | Scheduled | 5 | No | 1 | 5 |  | GENERAL - Inspection | 901.6 | Trim Ring missing. | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Front counter | Maroc & Luca Dumpling |  | 112 West Main Street 15 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151009 |  | Scheduled | 5 | No | 1 | 5 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Side dining | Maroc & Luca Dumpling |  | 112 West Main Street 15 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151010 |  | Scheduled | 5 | No | 1 | 5 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Front Doors (x2) | Grit Coffee |  | 112 West Main Street 1 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151010 |  | Scheduled | 5 | No | 1 | 5 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Grit Coffee |  | 112 West Main Street 1 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151010 |  | Scheduled | 5 | No | 1 | 5 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Kitchen (ABC) (No Date) | Grit Coffee |  | 112 West Main Street 1 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151010 |  | Scheduled | 5 | No | 1 | 5 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Side seating | Grit Coffee |  | 112 West Main Street 1 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151010 |  | Scheduled | 5 | No | 1 | 5 |  | ALTERNATIVE - Portable fire extinguishers for commercial cooking equipment | 904.11.5 |  | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) travel distance of commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.11.5.1 or 904.11.5.2, as applicable. | No Class K Can | Grit Coffee |  | 112 West Main Street 1 | 112 W MAIN ST | Dry-pipe sprinkler system |  | Entire Building | Present | More than one type present |  | Mixed use, other | Assembly, other |  | Side D | No | 3 | 0 | Enclosed building | 112 West Main Street
2019-08-15 | 201908151008 |  | Scheduled | 0 | Yes | 0.5 | 2 | [6 empty] | Royalty Eats |  | 820 CHERRY Avenue | 820 CHERRY AVE |  |  |  | None present |  | No | Mixed use, other | Mercantile, business, other |  | No | No | 1 | 0 | Enclosed building | 820 CHERRY Avenue
2019-08-20 | 201908201018 |  | Scheduled | 0 | Yes | 0.75 | 0 | [6 empty] | Moe's Original BBQ | 10829 | 2119 Ivy Road | 2119 IVY RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Assembly use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 2119 Ivy Road
2019-08-22 | 201908221019 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. |  | Tokyo Rose | 11971 | 2171 Ivy Road 13 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2019-08-22 | 201908221019 |  | Scheduled | 2 | No | 1 | 2 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Basement office (Fridge) | Tokyo Rose | 11971 | 2171 Ivy Road 13 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2019-08-22 | 201908221020 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Dining Wall | Taiwan Garden | 10811 | 2171 Ivy Road 9 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2019-08-22 | 201908221020 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Dining wall floor level @ electrical panel. | Taiwan Garden | 10811 | 2171 Ivy Road 9 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2019-08-22 | 201908221020 |  | Scheduled | 4 | No | 1 | 4 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Fount counter | Taiwan Garden | 10811 | 2171 Ivy Road 9 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2019-08-22 | 201908221020 |  | Scheduled | 4 | No | 1 | 4 |  | FUEL - Clearances | 603.1.7 |  | Working clearances between oil-fired appliances and electrical panel boards and equipment shall be in accordance with NFPA 70. Clearances between oil-fired equipment and oil supply tanks shall be in accordance with NFPA 31. | Water Heater | Taiwan Garden | 10811 | 2171 Ivy Road 9 | 2171 IVY RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side A/D | Row of stores | Assembly, other |  | Side C/D | No | 1 | 1 | Enclosed building | 2171 Ivy Road
2019-08-22 | 201908221022 |  | Scheduled | 3 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front counter | Chipotle |  | 953 EMMET North Street | 953 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 953 EMMET North Street
2019-08-22 | 201908221022 |  | Scheduled | 3 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen exit | Chipotle |  | 953 EMMET North Street | 953 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 953 EMMET North Street
2019-08-22 | 201908221022 |  | Scheduled | 3 | No | 1 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | At kitchen hood | Chipotle |  | 953 EMMET North Street | 953 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 953 EMMET North Street
2019-08-22 | 201908221021 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Unapproved conditions | 605.6 | Panel missing blank covers | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical Panel in upstairs office | McDonald's |  | 941 EMMET North Street | 941 EMMET ST N | Special hazard system, other |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 941 EMMET North Street
2019-08-22 | 201908221021 |  | Scheduled | 5 | No | 1 | 5 |  | FUEL - Clearances | 603.1.7 |  | Working clearances between oil-fired appliances and electrical panel boards and equipment shall be in accordance with NFPA 70. Clearances between oil-fired equipment and oil supply tanks shall be in accordance with NFPA 31. | Water Heater | McDonald's |  | 941 EMMET North Street | 941 EMMET ST N | Special hazard system, other |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 941 EMMET North Street
2019-08-22 | 201908221021 |  | Scheduled | 5 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Basement office | McDonald's |  | 941 EMMET North Street | 941 EMMET ST N | Special hazard system, other |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 941 EMMET North Street
2019-08-22 | 201908221021 |  | Scheduled | 5 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Dining area x 3 | McDonald's |  | 941 EMMET North Street | 941 EMMET ST N | Special hazard system, other |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 941 EMMET North Street
2019-08-22 | 201908221021 |  | Scheduled | 5 | No | 1 | 5 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Dining side exit | McDonald's |  | 941 EMMET North Street | 941 EMMET ST N | Special hazard system, other |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 941 EMMET North Street
2019-08-23 | 201908231028 |  | Scheduled | 3 | No | 0.75 | 3 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Front Door | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2019-08-23 | 201908231028 |  | Scheduled | 3 | No | 0.75 | 3 |  | ELECTRICAL - Unapproved conditions | 605.6 | In ceiling above both front windows. x 2 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Front Windows | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2019-08-23 | 201908231028 |  | Scheduled | 3 | No | 0.75 | 3 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency combo | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Rear kitchen exit | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2019-08-23 | 201908231029 |  | Scheduled | 0 | No | 0.75 | 4 |  | PORTABLE - General requirements | 906.2 | 2020-09-19 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | (7/18) | Bread Works |  | 923 Preston Avenue | 923 PRESTON AVE | Special hazard system, other |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 923 Preston Avenue
2019-08-23 | 201908231029 |  | Scheduled | 0 | No | 0.75 | 4 |  | ELECTRICAL - Working space and clearance | 605.3 | All last panels. | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Mech Room | Bread Works |  | 923 Preston Avenue | 923 PRESTON AVE | Special hazard system, other |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 923 Preston Avenue
2019-08-23 | 201908231029 |  | Scheduled | 0 | No | 0.75 | 4 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | No record of cleaning | Bread Works |  | 923 Preston Avenue | 923 PRESTON AVE | Special hazard system, other |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 923 Preston Avenue
2019-08-23 | 201908231029 |  | Scheduled | 0 | No | 0.75 | 4 |  | ALTERNATIVE - Extinguishing system service | 904.11.6.2 | 2020-09-19 | Automatic fire-extinguishing systems shall be serviced at least every six months and after activation of the system. Inspection shall be by qualified individuals, and a certificate of inspection shall be forwarded to the fire code official upon completion. | (07/18) | Bread Works |  | 923 Preston Avenue | 923 PRESTON AVE | Special hazard system, other |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 923 Preston Avenue
2019-08-23 | 201908231027 |  | Scheduled | 1 | No | 0.75 | 3 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Mech Room | Sticks Kebob Shop |  | 917 Preston Avenue A | 917 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 917 Preston Avenue
2019-08-23 | 201908231027 |  | Scheduled | 1 | No | 0.75 | 3 |  | FUEL - Clearances | 603.1.7 | Combustible storage around gas water heater. | Working clearances between oil-fired appliances and electrical panel boards and equipment shall be in accordance with NFPA 70. Clearances between oil-fired equipment and oil supply tanks shall be in accordance with NFPA 31. | Mech Room | Sticks Kebob Shop |  | 917 Preston Avenue A | 917 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 917 Preston Avenue
2019-08-23 | 201908231027 |  | Scheduled | 1 | No | 0.75 | 3 |  | OCCUPANT - Posting of occupant load | 1004.3 | No occupancy posted. | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. |  | Sticks Kebob Shop |  | 917 Preston Avenue A | 917 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 917 Preston Avenue
2019-08-26 | 201908261038 |  | Scheduled | 2 | No | 0.5 | 9 | [6 empty] | Shebeen |  | 247 RIDGE MCINTIRE Road | 247 RIDGE MCINTIRE RD | Wet-pipe sprinkler system | Wet-pipe sprinkler system |  | None present |  | Side B | Mixed use, other | Restaurant or cafeteria |  | Side B/C | No | 1 | 1 | Enclosed building | 247 RIDGE MCINTIRE Road
2019-08-26 | 201908261031 |  | Scheduled | 0 | Yes | 0.5 | 2 | [6 empty] | McDonalds |  | 475 RIDGE MCINTIRE Road | 475 RIDGE MCINTIRE Road |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 475 RIDGE MCINTIRE Road
2019-08-26 | 201908261036 |  | Scheduled | 2 | No | 0.5 | 2 |  | FUEL - Clearances | 603.1.7 | Combustible storage at water heater. | Working clearances between oil-fired appliances and electrical panel boards and equipment shall be in accordance with NFPA 70. Clearances between oil-fired equipment and oil supply tanks shall be in accordance with NFPA 31. | Water Heater | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2019-08-26 | 201908261036 |  | Scheduled | 2 | No | 0.5 | 2 |  | FUEL - Clearances | 603.1.7 | Combustible storage at water heater. | Working clearances between oil-fired appliances and electrical panel boards and equipment shall be in accordance with NFPA 70. Clearances between oil-fired equipment and oil supply tanks shall be in accordance with NFPA 31. | Water Heater | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2019-08-26 | 201908261036 |  | Scheduled | 2 | No | 0.5 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 | Need proof of cleaning. | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Wet-pipe sprinkler system |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2019-08-26 | 201908261036 |  | Scheduled | 2 | No | 0.5 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 | Need proof of cleaning. | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Maharaja |  | 139 ZAN Road | 139 ZAN RD | Special hazard system, other |  |  | None present |  | Side C | Row of stores | Restaurant or cafeteria |  | Side C/ 149 Zan Rd | No | 1 | 0 | Enclosed building | 139 ZAN Road
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo battery backup. | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Rear exit (dining) | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency Combo battery backup. | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Rear exit (dining) | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Side dining (Right of Host desk) | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Side dining (Right of Host desk) | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Hallway (restrooms) | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Hallway (restrooms) | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Kitchen exit | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Kitchen exit | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | ELECTRICAL - Extension cords | 605.5 | 2 extension cords. One cord running into ceiling area. | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen at water heater | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Special hazard system, other | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261037 |  | Scheduled | 5 | No | 0.5 | 5 |  | ELECTRICAL - Extension cords | 605.5 | 2 extension cords. One cord running into ceiling area. | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen at water heater | Sushi King |  | 171 SEMINOLE Court | 171 SEMINOLE CT | Wet-pipe sprinkler system | Special hazard system, other,Wet-pipe sprinkler system |  | None present |  | Side A | Row of stores | Restaurant or cafeteria |  | Side C | No | 1 | 0 | Enclosed building | 171 SEMINOLE Court
2019-08-26 | 201908261034 |  | Scheduled | 1 | No | 0.5 | 1 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Panel L missing blank covers | Raising Cane's |  | 1805 EMMET North Street | 1805 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1805 EMMET North Street
2019-08-26 | 201908261035 |  | Scheduled | 1 | No | 0.5 | 1 |  |  |  | Exit sign not illuminated. |  | Front Door | Milan Indian Cuisine | 324 | 1817 EMMET North Street | 1817 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1817 EMMET North Street
2019-08-26 | 201908261030 |  | Scheduled | 2 | No | 0.5 | 3 | [6 empty] | Wendy's |  | 416 4TH Northwest Street | 416 4TH ST NW |  |  |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 416 4TH Northwest Street
2019-08-26 | 201908261039 |  | Scheduled | 2 | No | 1 | 2 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Front Door | Tavola | 10783 | 826 HINTON Avenue A | 826 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 826 HINTON Avenue
2019-08-26 | 201908261039 |  | Scheduled | 2 | No | 1 | 2 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. |  | Tavola | 10783 | 826 HINTON Avenue A | 826 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 826 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Hallway @ Restroom | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | EXIT - Power source | 1011.6.3 |  | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Hallway @ Restroom | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen (Fridge) | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen (Fridge) | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | No Date | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | No Date | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Class K (No Tag) | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Class K (No Tag) | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Class K (Kitchen) | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Class K (Kitchen) | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency combo battery backup. | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Deck (rear server counter) | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency combo battery backup. | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Deck (rear server counter) | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | 2nd Floor server closet (ABC no tag) | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | 2nd Floor server closet (ABC no tag) | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Needs annual inspection (7/19/18) | The Local |  | 824 HINTON B | 824 HINTON AVE | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-26 | 201908261040 |  | Scheduled | 8 | No | 1 | 8 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Needs annual inspection (7/19/18) | The Local |  | 824 HINTON B | 824 HINTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 2 | 0 | Enclosed building | 824 HINTON Avenue
2019-08-27 | 201908271045 |  | Scheduled | 6 | No | 1 | 6 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency battery backup. | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | Front | Druknya House |  | 2208 FONTAINE Avenue | 2208 FONTAINE AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 2208 FONTAINE Avenue
2019-08-27 | 201908271045 |  | Scheduled | 6 | No | 1 | 6 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front Open sign | Druknya House |  | 2208 FONTAINE Avenue | 2208 FONTAINE AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 2208 FONTAINE Avenue
2019-08-27 | 201908271045 |  | Scheduled | 6 | No | 1 | 6 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Host station | Druknya House |  | 2208 FONTAINE Avenue | 2208 FONTAINE AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 2208 FONTAINE Avenue
2019-08-27 | 201908271045 |  | Scheduled | 6 | No | 1 | 6 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. |  | Druknya House |  | 2208 FONTAINE Avenue | 2208 FONTAINE AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 2208 FONTAINE Avenue
2019-08-27 | 201908271045 |  | Scheduled | 6 | No | 1 | 6 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Rear wall (modem) | Druknya House |  | 2208 FONTAINE Avenue | 2208 FONTAINE AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 2208 FONTAINE Avenue
2019-08-27 | 201908271045 |  | Scheduled | 6 | No | 1 | 6 |  | FUELED - General | 313.1 |  | Fueled equipment including, but not limited to, motorcycles, mopeds, lawn-care equipment, portable generators and portable cooking equipment, shall not be stored, operated or repaired within a building. Exceptions: 1.Buildings or rooms constructed for such use in accordance with the International Building Code. 2.Where allowed by Section 314. 3.Storage of equipment utilized for maintenance purposes is allowed in approved locations when the aggregate fuel capacity of the stored equipment does not exceed 10 gallons (38 L) and the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. | leaf blower stored in rear hallway | Druknya House |  | 2208 FONTAINE Avenue | 2208 FONTAINE AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 2208 FONTAINE Avenue
2019-09-03 | 201909031050 |  | Scheduled | 0 | Yes | 0.5 | 1 | [6 empty] | Burger King | 13379 | 1181 5TH Southwest Street | 1181 5TH ST SW | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | NO | No | 1 | 0 | Enclosed building | 1181 5TH Southwest Street
2019-09-03 | 201909031052 |  | Scheduled | 0 | Yes | 0.5 | 3 | [6 empty] | La Joya |  | 1145 5TH Southwest Street | 1145 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1145 5TH Southwest Street
2019-09-03 | 201909031054 |  | Scheduled | 0 | Yes | 0.5 | 3 | [6 empty] | Jade Garden |  | 1139 5TH Southwest Street | 1139 5TH ST SW |  |  |  | Present | Smoke | No | Mixed use, other | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 1139 5TH Southwest Street
2019-09-03 | 201909031056 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front (Open Sign) | Anna's Italian Restaurant |  | 115 MAURY Avenue | 115 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 115 MAURY Avenue
2019-09-03 | 201909031056 |  | Scheduled | 5 | No | 1 | 5 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Side wall (dining area) | Anna's Italian Restaurant |  | 115 MAURY Avenue | 115 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 115 MAURY Avenue
2019-09-03 | 201909031056 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen hood light | Anna's Italian Restaurant |  | 115 MAURY Avenue | 115 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 115 MAURY Avenue
2019-09-03 | 201909031056 |  | Scheduled | 5 | No | 1 | 5 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Outlet (Kitchen wall behind hood system) | Anna's Italian Restaurant |  | 115 MAURY Avenue | 115 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 115 MAURY Avenue
2019-09-03 | 201909031056 |  | Scheduled | 5 | No | 1 | 5 |  | OCCUPANT - Posting of occupant load | 1004.3 | Contact NDS for Occupant Load Permit 434-970-3182 | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. | Need Occupant Load Permit | Anna's Italian Restaurant |  | 115 MAURY Avenue | 115 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 115 MAURY Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Abatement of electrical hazards | 605.1 |  | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the responsible code official. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. | Rice pot (Cord end) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen (refrigerator) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Kitchen outlet (at refrigerator) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical panel missing blanks (Panel B) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Working space and clearance | 605.3 |  | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. Exceptions: 1.Where other dimensions are required or allowed by NFPA 70. 2.Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Rear store room | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front (drink box at fan) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front (TV) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | COMMERCIAL - Grease accumulation | 609.3.3.2 |  | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned. | Hood Needs cleaning | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-03 | 201909031055 |  | Scheduled | 9 | No | 1 | 9 |  | ALTERNATIVE - Commercial cooking systems | 904.11 | System needs to be repair/replaced to meet UL 300. | The automatic fire-extinguishing system for commercial cooking systems shall be of a type recognized for protection of commercial cooking equipment and exhaust systems of the type and arrangement protected. Preengineered automatic dry- and wet-chemical extinguishing systems shall be tested in accordance with UL 300 and listed and labeled for the intended application. Other types of automatic fire-extinguishing systems shall be listed and labeled for specific use as protection for commercial cooking operations. The system shall be installed in accordance with this code, its listing and the manufacturer’s installation instructions. Automatic fire-extinguishing systems of the following types shall be installed in accordance with the referenced standard indicated, as follows: 1.Carbon dioxide extinguishing systems, NFPA 12. 2.Automatic sprinkler systems, NFPA 13. 3.Foam-water sprinkler system or foam-water spray systems, NFPA 16. 4.Dry-chemical extinguishing systems, NFPA 17. 5.Wet-chemical extinguishing systems, NFPA 17A. Exception: Factory-built commercial cooking recirculating systems that are tested in accordance with UL 710B and listed, labeled and installed in accordance with Section 304.1 of the International Mechanical Code. | System Red Tag (Non UL 300) | Yuan Ho |  | 117 Maury Avenue | 117 MAURY AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 117 Maury Avenue
2019-09-04 | 201909041062 |  | Scheduled | 3 | No | 0.5 | 3 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Ceiling food prep | Belle Coffee & Wine |  | 407 MONTICELLO Road | 407 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 407 MONTICELLO Road
2019-09-04 | 201909041062 |  | Scheduled | 3 | No | 0.5 | 3 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical panel missing blanks | Belle Coffee & Wine |  | 407 MONTICELLO Road | 407 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 407 MONTICELLO Road
2019-09-04 | 201909041062 |  | Scheduled | 3 | No | 0.5 | 3 |  | PORTABLE - Hangers and brackets | 906.7 |  | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions. | Class K | Belle Coffee & Wine |  | 407 MONTICELLO Road | 407 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 407 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | 3rd floor landing | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | 3rd floor landing | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency Combo inoperable battery backup | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | 3rd floor landing | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 | Exit/Emergency Combo inoperable battery backup | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | 3rd floor landing | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 | Corrected | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | 3rd floor (projector) | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 | Corrected | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | 3rd floor (projector) | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | Sprinkler system needs annual inspection | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | Sprinkler system needs annual inspection | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | Fire alarm system | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | GENERAL - Standards | 901.6.1 |  | Fire protection systems shall be inspected, tested and maintained in accordance with the referenced standards listed in Table 901.6.1. | Fire alarm system | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | x 2 hoods | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | COMMERCIAL - Cleaning | 609.3.3 |  | Hoods, grease-removal devices, fans, ducts and other appurtenances shall be cleaned at intervals as required by Sections 609.3.3.1 through 609.3.3.3. | x 2 hoods | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Exterior basement (stairs) | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Exterior basement (stairs) | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Exterior basement (walkway) | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Wet-pipe sprinkler system | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041061 |  | Scheduled | 7 | No | 1 | 8 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Exterior basement (walkway) | Junction |  | 421 MONTICELLO Road | 421 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | Side B | Not mixed use | Restaurant or cafeteria |  | Side B | No | 2 | 1 | Enclosed building | 421 MONTICELLO Road
2019-09-04 | 201909041060 |  | Scheduled | 1 | No | 0.5 | 1 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical Panel Missing Blanks | Barbie's Burrito Barn | 21240 | 201 Avon Street | 201 AVON ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 201 Avon Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Front exit counter | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | EXIT - Illumination | 1011.3 |  | Exit signs shall be internally or externally illuminated. Exception: Tactile signs required by Section 1011.4 need not be provided with illumination. | Front exit counter | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Lights strands hanging from sprinkler pipe (deli) | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | GENERAL - Inspection | 901.6 |  | To the extent that equipment, systems, devices, and safeguards, such as fire detection, alarm and extinguishing systems, which were provided and approved by the building official when constructed, shall be maintained in an operative condition at all times. And where such equipment, systems, devices, and safeguards are found not to be in an operative condition, the fire official shall order all such equipment to be rendered safe in accordance with the USBC. | Lights strands hanging from sprinkler pipe (deli) | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen @ hood system | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Kitchen @ hood system | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | UNSAFE - General | 110.1 | Combustible storage around gas HVAC unit | The fire official shall order the following dangerous or hazardous conditions or materials to be removed or remedied in accordance with the SFPC: 1.Dangerous conditions which are liable to cause or contribute to the spread of fire in or on said premises, building or structure, or to endanger the occupants thereof. 2.Conditions which would interfere with the efficiency and use of any fire protection equipment. 3.Obstructions to or on fire escapes, stairs, passageways, doors or windows, which are liable to interfere with the egress of occupants or the operation of the fire department in case of fire. 4.Accumulations of dust or waste material in air conditioning or ventilating systems or grease in kitchen or other exhaust ducts. 5.Accumulations of grease on kitchen cooking equipment, or oil, grease or dirt upon, under or around any mechanical equipment. 6.Accumulations of rubbish, waste, paper, boxes, shavings, or other combustible materials, or excessive storage of any combustible material. 7.Hazardous conditions arising from defective or improperly used or installed electrical wiring, equipment or appliances. 8.Hazardous conditions arising from defective or improperly used or installed equipment for handling or using combustible, explosive or otherwise hazardous materials. 9.Dangerous or unlawful amounts of combustible, explosive or otherwise hazardous materials. 10.All equipment, materials, processes or operations which are in violation of the provisions and intent of this code. | HVAC Rear | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | UNSAFE - General | 110.1 | Combustible storage around gas HVAC unit | The fire official shall order the following dangerous or hazardous conditions or materials to be removed or remedied in accordance with the SFPC: 1.Dangerous conditions which are liable to cause or contribute to the spread of fire in or on said premises, building or structure, or to endanger the occupants thereof. 2.Conditions which would interfere with the efficiency and use of any fire protection equipment. 3.Obstructions to or on fire escapes, stairs, passageways, doors or windows, which are liable to interfere with the egress of occupants or the operation of the fire department in case of fire. 4.Accumulations of dust or waste material in air conditioning or ventilating systems or grease in kitchen or other exhaust ducts. 5.Accumulations of grease on kitchen cooking equipment, or oil, grease or dirt upon, under or around any mechanical equipment. 6.Accumulations of rubbish, waste, paper, boxes, shavings, or other combustible materials, or excessive storage of any combustible material. 7.Hazardous conditions arising from defective or improperly used or installed electrical wiring, equipment or appliances. 8.Hazardous conditions arising from defective or improperly used or installed equipment for handling or using combustible, explosive or otherwise hazardous materials. 9.Dangerous or unlawful amounts of combustible, explosive or otherwise hazardous materials. 10.All equipment, materials, processes or operations which are in violation of the provisions and intent of this code. | HVAC Rear | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | ELECTRICAL - Multiplug adapters | 605.4 | unfused multi outlet plug | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Staff fridge | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | ELECTRICAL - Multiplug adapters | 605.4 | unfused multi outlet plug | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | Staff fridge | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | 2nd floor landing | Feast |  | 416 West Main Street H | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051064 |  | Scheduled | 6 | No | 1 | 6 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | 2nd floor landing | Feast |  | 416 West Main Street H | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051065 |  | Scheduled | 2 | No | 1 | 2 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency combo inoperable battery backup | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | W Main Exit | Orzo |  | 416 West Main Street | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051065 |  | Scheduled | 2 | No | 1 | 2 |  | EXIT - Power source | 1011.6.3 | Exit/Emergency combo inoperable battery backup | Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. Exception: Approved exit sign illumination means that provide continuous illumination independent of external power sources for a duration of not less than 90 minutes, in case of primary power loss, are not required to be connected to an emergency electrical system. | W Main Exit | Orzo |  | 416 West Main Street | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051065 |  | Scheduled | 2 | No | 1 | 2 |  | OCCUPANT - Posting of occupant load | 1004.3 |  | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. |  | Orzo |  | 416 West Main Street | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051065 |  | Scheduled | 2 | No | 1 | 2 |  | OCCUPANT - Posting of occupant load | 1004.3 |  | Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. |  | Orzo |  | 416 West Main Street | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051066 |  | Scheduled | 2 | No | 0.5 | 2 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen ceiling | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051066 |  | Scheduled | 2 | No | 0.5 | 2 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Kitchen ceiling | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051066 |  | Scheduled | 2 | No | 0.5 | 2 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | upstairs water heater | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Special hazard system, other |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051066 |  | Scheduled | 2 | No | 0.5 | 2 |  | ELECTRICAL - Multiplug adapters | 605.4 |  | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with NFPA 70 shall be prohibited. | upstairs water heater | Monsoon Siam TOGOGO | 14658 | 416 West Main Street E | 416 W MAIN ST | Wet-pipe sprinkler system |  |  | None present |  | A/B Corner | Row of stores | Restaurant or cafeteria |  | Side A (Orzo) | No | 1 | 0 | Enclosed building | 416 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | MEANS - Emergency power for illumination | 1006.3 |  | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas: 1.Aisles and unenclosed egress stairways in rooms and spaces that require two or more means of egress. 2.Corridors, interior exit stairways and ramps and exit passageways in buildings required to have two or more exits. 3.Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits. 4.Interior exit discharge elements, as permitted in Section 1027.1, in buildings required to have two or more exits. 5.Exterior landings as required by Section 1008.1.6 for exit discharge doorways in buildings required to have two or more exits. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 604. | Office 2nd floor | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Front/Host desk | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | kitchen light switch | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | PORTABLE - General requirements | 906.2 |  | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1.The travel distance to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2.Thirty-day inspections shall not be required and maintenance shall be allowed to be once every three years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: 2.1.Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. 2.2.Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. 2.3.The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. 2.4.Electronic monitoring devices and supervisory circuits shall be tested every three years when extinguisher maintenance is performed. 2.5.A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. 3.In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | ABC (6/17) | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Bar dining area (window wreaths) | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical panel missing blanks | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | GENERAL REQUIREMENTS - Securing compressed gas containers, cylinders and tanks | 3003.5.3 |  | Securing compressed gas containers, cylinders and tanks. Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: (see manual for further details) | Basement | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | UNSAFE - General | 110.1 | Combustible storage around gas water heater. | The fire official shall order the following dangerous or hazardous conditions or materials to be removed or remedied in accordance with the SFPC: 1.Dangerous conditions which are liable to cause or contribute to the spread of fire in or on said premises, building or structure, or to endanger the occupants thereof. 2.Conditions which would interfere with the efficiency and use of any fire protection equipment. 3.Obstructions to or on fire escapes, stairs, passageways, doors or windows, which are liable to interfere with the egress of occupants or the operation of the fire department in case of fire. 4.Accumulations of dust or waste material in air conditioning or ventilating systems or grease in kitchen or other exhaust ducts. 5.Accumulations of grease on kitchen cooking equipment, or oil, grease or dirt upon, under or around any mechanical equipment. 6.Accumulations of rubbish, waste, paper, boxes, shavings, or other combustible materials, or excessive storage of any combustible material. 7.Hazardous conditions arising from defective or improperly used or installed electrical wiring, equipment or appliances. 8.Hazardous conditions arising from defective or improperly used or installed equipment for handling or using combustible, explosive or otherwise hazardous materials. 9.Dangerous or unlawful amounts of combustible, explosive or otherwise hazardous materials. 10.All equipment, materials, processes or operations which are in violation of the provisions and intent of this code. | Water heater | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | ELECTRICAL - Extension cords | 605.5 |  | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Basement restroom hall | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | UNSAFE - General | 110.1 | Combustible storage around gas HVAC system. | The fire official shall order the following dangerous or hazardous conditions or materials to be removed or remedied in accordance with the SFPC: 1.Dangerous conditions which are liable to cause or contribute to the spread of fire in or on said premises, building or structure, or to endanger the occupants thereof. 2.Conditions which would interfere with the efficiency and use of any fire protection equipment. 3.Obstructions to or on fire escapes, stairs, passageways, doors or windows, which are liable to interfere with the egress of occupants or the operation of the fire department in case of fire. 4.Accumulations of dust or waste material in air conditioning or ventilating systems or grease in kitchen or other exhaust ducts. 5.Accumulations of grease on kitchen cooking equipment, or oil, grease or dirt upon, under or around any mechanical equipment. 6.Accumulations of rubbish, waste, paper, boxes, shavings, or other combustible materials, or excessive storage of any combustible material. 7.Hazardous conditions arising from defective or improperly used or installed electrical wiring, equipment or appliances. 8.Hazardous conditions arising from defective or improperly used or installed equipment for handling or using combustible, explosive or otherwise hazardous materials. 9.Dangerous or unlawful amounts of combustible, explosive or otherwise hazardous materials. 10.All equipment, materials, processes or operations which are in violation of the provisions and intent of this code. | HVAC closet basement | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | ELECTRICAL - Unapproved conditions | 605.6 |  | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | HVAC closet | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-05 | 201909051063 |  | Scheduled | 5 | No | 1 | 12 |  | DECORATIVE - General | 807.4.1 |  | All of the following requirements shall apply to all Group A and E occupancies and Group I-4 day care facilities regulated by Sections 807.4.2 through 807.4.4: 1.Explosive or highly flammable materials. Furnishings or decorative materials of an explosive or highly flammable character shall not be used. 2.Fire-retardant coatings. Fire-retardant coatings in existing buildings shall be maintained so as to retain the effectiveness of the treatment under service conditions encountered in actual use. 3.Obstructions. Furnishings or other objects shall not be placed to obstruct exits, access thereto, egress therefrom or visibility thereof. | Ceiling covering | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-09-06 | 201909061070 |  | Scheduled | 3 | No | 0.5 | 5 | [6 empty] | Beer Run | 21409 | 156 Carlton Road 2 203 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-09-06 | 201909061071 |  | Scheduled | 7 | No | 0.5 | 7 | [6 empty] | Pad Thai Restaurant | 4057 | 156 Carlton Road 202 | 156 Carlton Rd |  |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 156 Carlton Road
2019-09-06 | 201909061068 |  | Scheduled | 2 | No | 0.5 | 3 | [6 empty] | Moose's | 4269 | 1710 Monticello Road | 1710 MONTICELLO RD | Special hazard system, other | Special hazard system, other |  | None present |  | No | Mixed use, other | Assembly, other |  | No | No | 1 | 0 | Enclosed building | 1710 Monticello Road
2019-09-06 | 201909061069 |  | Scheduled | 0 | Yes | 0.5 | 4 | [6 empty] | Belmont Pizza |  | 221 CARLTON Road 10 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-09-06 | 201909061072 |  | Scheduled | 7 | No | 0.5 | 8 | [6 empty] | Cactus |  | 221 Carlton Road 11 | 221 CARLTON RD |  |  | throughout | Present | Smoke |  | Row of stores | Restaurant or cafeteria |  |  |  | 1 | 0 | Enclosed building | 221 CARLTON Road
2019-09-10 | 201909101079 |  | Scheduled | 0 | Yes | 0.5 | 3 | [6 empty] | Kentucky Fried Chicken |  | 1705 EMMET North Street | 1705 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1705 North EMMET Street
2019-09-10 | 201909101080 |  | Scheduled | 1 |  | 0.5 | 3 | [6 empty] | Brother's Bar & Grill |  | 2104 ANGUS Road | 2104 ANGUS RD | Other sprinkler system |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 2104 ANGUS Road
2019-09-20 | 201909201119 |  | Scheduled | 1 | No | 0.25 | 4 | [6 empty] | Keevil &Keevil Grocery & Kitchen |  | 703 Hinton Avenue | 703 Hinton Ave |  |  |  | None present |  | No | Residential use | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 703 Hinton Avenue
2019-10-15 | 201910151194 |  | Scheduled | 0 | Yes | 0.5 | 8 | [6 empty] | Downtown Grille |  | 201 West MAIN Street | 201 W MAIN ST | Wet-pipe sprinkler system | Wet-pipe sprinkler system | Limited Coverage | Present | Smoke | Side D | Office use | Restaurant or cafeteria |  | Side D | No | 3 | 0 | Enclosed building | 201 West MAIN Street
2019-10-15 | 201910151191 |  | Scheduled | 0 | Yes | 0.5 | 6 | [6 empty] | Citizen Bowl Shop |  | 223 West MAIN Street | 223 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 223 West MAIN Street
2019-10-15 | 201910151195 |  | Scheduled | 0 | Yes | 0.5 | 2 | [6 empty] | Popeye's |  | 1709 EMMET North Street A | 1709 EMMET ST N | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 1709 EMMET North Street
2019-10-15 | 201910151196 |  | Scheduled | 0 | Yes | 0.05 | 11 | [6 empty] | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Wet-pipe sprinkler system |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-10-15 | 201910151196 |  | Scheduled | 0 | Yes | 0.05 | 11 | [6 empty] | Aberdeen Barn |  | 2018 HOLIDAY Drive | 2018 Holiday Drive | Special hazard system, other |  |  | None present |  | Side A | Not mixed use | Restaurant or cafeteria |  | Side A | No | 1 | 0 | Enclosed building | 2018 HOLIDAY Drive
2019-10-15 | 201910151193 |  | Scheduled | 0 | Yes | 0.5 | 8 | [6 empty] | The Bebedero |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-10-15 | 201910151192 |  | Scheduled | 0 | Yes | 0.5 | 6 | [6 empty] | The Whiskey Jar |  | 227 West MAIN Street | 227 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 2 | 0 | Enclosed building | 227 West MAIN Street
2019-11-04 | 201911041238 |  | Scheduled | 5 | No | 0.33 | 12 | [6 empty] | Tavern & Grocery |  | 333 West Main Street | 333 W MAIN ST | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 2 | 1 | Enclosed building | 333 West Main Street
2019-11-15 | 201911151245 |  | Scheduled | 0 | Yes |  | 3 | [6 empty] | Brother's Bar & Grill |  | 2104 ANGUS Road | 2104 ANGUS RD | Other sprinkler system |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 1 | Enclosed building | 2104 ANGUS Road
2019-12-06 | 201912061290 |  | Scheduled | 3 | No | 0.29 | 3 | [6 empty] | Mona Lisa Pasta | 10128 | 921 PRESTON Avenue A | 921 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 921 PRESTON Avenue
2019-12-06 | 201912061289 |  | Scheduled | 0 | No | 0.21 | 3 | [6 empty] | Sticks Kebob Shop |  | 917 Preston Avenue A | 917 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 917 Preston Avenue
2019-12-06 | 201912061291 |  | Scheduled | 0 | Yes | 0.24 | 4 | [6 empty] | Bread Works |  | 923 Preston Avenue | 923 PRESTON AVE | Special hazard system, other |  |  | None present |  | No | Row of stores | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 923 Preston Avenue
2020-01-07 | 202001071336 |  | Scheduled | 0 | Yes | 0.24 | 3 | [6 empty] | Sticks Kebob Shop |  | 917 Preston Avenue A | 917 PRESTON AVE | Special hazard system, other | Special hazard system, other |  | None present |  | No | Not mixed use | Restaurant or cafeteria |  | No | No | 1 | 0 | Enclosed building | 917 Preston Avenue

## Notes
Inspections data is stored in a hierarchy in the records managemnt system used by CFD.
The hierarchy is Locations>Occupants>Inspections
Locations are physical addresses or buildings
Occupants are leasees or owners of buildings who operate a business within it
Inspections are findings of certified fire inspectors during regularly scheduled inspections of occupants operating at locations
Fire code violations are common and do not reflect poor health or safety standards in an establishment
This data is for project use only--do not distribute in other locations